## Sheet1
Annexure- I
FORMAT FOR SUBMITTING TECHNICAL BID (Please mark Yes / No should be marked against each aspect of Alarm system)
Basic Technical Specification & compliance for Bidder
Sl | Technical Specification Compliance for Fire and Electronic intruder Alarm System(Component and Description of Specification) | Compliance Yes/No
CONTROL PANEL
1 | LCD based minimum 12+1 fully programmable zone control panel with built in GSM speech dialer with automatic arming and disarming with remote access through telephone
2 | Microcontroller based
3 | Minimum 12+1 zones
4 | Inbuilt GSM based speech and SMS dial up
5 | Minimum 12 zones programmable as delay, immediate, panic or fire
6 | One tamper zone
7 | Separate remote key pad with 12X4 LCD display or more
8 | Separate zone for fire detection and provision for connection of fire alarm system
9 | Separate main control station for connection terminals and power supply units
10 | Automatic arming and disarming facility
11 | Can be operated through mobile and telephone line
12 | Electrical devises can also be switched on or off through remote key pad
13 | Built in battery backup
14 | Zone omitting facility
15 | Silent arming and night mode arming
16 | Intrusion lock with time and date
17 | Power failure indication
18 | Blown fuse indication on LCD display on LED blinking on panel
19 | Multiple sounder output
20 | Distinct interrupted sounder output for fire alarm
21 | Battery strength display with audio indication in case of low battery
22 | GSM signal strength display
23 | Walk test mode
24 | Individual zone status is indicated in display
25 | Independent entry delay time 2 to 240 sec
26 | Independent exit delay time 2 to 240 sec
27 | Sounder time 2 to 20 minutes and multiple sounder outputs
28 | Speaker wire cut detection for all sensors and hooters and speakers
29 | Support combination of hooters and speakers
30 | Battery backup for 36 hours
31 | Automatic switch off to battery in case of AC power failure
32 | Automatic battery charging once the AC power is restored
33 | ERTL certified.
Sl. | SMOKE SENSOR & HEAT SENSOR
1 | Automatic Drift compensation
2 | Dust tolerant chamber provides optimum detection performance and minimal nuisance alarm between maintenance visit
3 | Multifunction handheld remote programming and test tool
4 | Sensitivity remotely programmable
5 | Digital addressing capability
6 | Remotely implemented advance maintenance features
Read and write last maintenance date
Read chamber contamination level
Read thermal element value alarm test
7 | Selectable blink/no blink LED option via hand held tool
8 | Photoelectric multi-criteria photo-thermal with 58 degree C and 78 degree C fixed and rate of raise thermal detector
9 | 8 to 30 VDC operating range enable operation in both fire and security system
10 | -30 to +70 degree C operating temperature range
11 | Multi-functional alarm – normal bio color LED indicator
12 | EN 54 certified
13 | Make -
Sl. | AUTOMATIC TELEPHONE DIALER & BUILT IN VOICE & SMS GSM DIALER
1 | GSM speech & SMS dialer
2 | Microcontroller base
3 | 2 speech / voice messages
4 | Separate intrusion & fire messages
5 | Minimum 10 programmable phone numbers upto 12 digits for intrusion and fire message
6 | 20 sec recording time for each message
7 | Alarm SMS with alarm type, zone number with time and date information
8 | System status SMS for arm and disarm
9 | Power status SMS for AC power on and off, low battery
10 | User editable name and address for alarm SMS
11 | Message playback, telephone no. editing facility, long volatile memory
12 | Retention of programmed data in case of power failure
13 | Highest priority for condition dialing and silent alarming
SL NO | ELECTRICAL
1 | Quiescent current: 30 mA Max.
2 | Quiescent current with backlit LCD: 90 mA Max.
3 | MAIN CONTROL STATION WITH ONE REMOTE KEY PAD
4 | Quiescent current: 300 mA
5 | Quiescent current with backlit LCD: 360 mA
6 | Current with dialing: 530 mA Max.
7 | Maximum sounder 1 current output : 1A
8 | Maximum sounder 2 current output : 1A
9 | Remote key pads : Up to three
10 | Non-volatile Memory : Programming and Log
11 | Zone response time : <500ms
12 | Zone Loop Resistance : <5k ohm for NORMALLY CLOSED
13 | Mains supply Voltage : 220+10%-15% 50Hz
14 | Total current Output: 2A at 220V AC or 4A at 220V AC
15 | Battery Voltage : 12V DC
16 | Battery type : SMF Rechargeable
17 | Battery Recharge Voltage: 13.8V +/-0.2V DC
18 | ENVIRONMENTAL
19 | Operating Temperature: 0C to 45C
20 | Storage Temperature: -20C to 60C
21 | Maximum humidity: 95% non-condensing
Sl No. | MAGNETIC CONTACT SENSOR
1 | Operating Gap: 15MM min
2 | Contact Rating: 10W, 12/24VDC, 0.5A
3 | Contact O/P : Normally Closed
4 | 4 wire temper loop
Sl No. | PIR SENSOR
1 | Dual Element Pyroelectric sensor
2 | Latest Technology Digital Signal Processor (DSP)
3 | Pet Immunity up to 25 kg.
4 | Detection Range 15m
5 | Detection angle 110°
6 | Sealed optics
7 | Excellent RFI and EMI Immunity
8 | Selectable Pulse Count
9 | Walk Test
10 | Detection range: 15m, 110°
11 | RFI Immunity: Ave. 20V/m (10~1000MHz)
12 | Power Supply: 9 ~ 16V DC, 12V Typical
13 | Current Consumption: 20mA, 12V DC
14 | Alarm Output: NC/NO 30V DC, 0.2A max.
15 | Alarm Duration: 2 seconds
16 | Pulse Count: Single/Double
17 | Tamper Switch: Cover Open activation
18 | Operating Temperature: 0° to 50° Celsius
19 | Walk Test LED: Red, can disable
20 | Temperature: Automatic using
21 | Compensation: NTC thermostat
22 | Detection Speed: 0.3 to 1 m/s
23 | Reverse Polarity Protection: Through Diode
Sl No. | PANIC SWITCH
1 | Automatic reset (no key required)
2 | Micro switch technology
3 | In-built tamper switch
4 | Contact O/P: NORMALLY CLOSED
5 | Technology: micro-switch with roller
6 | Tamper Switch: installed
Sl No. | HOOTER
1 | High power 130 db
2 | 4 wired (with tamper loop)
3 | Low current consumption
4 | Available in 12V DC and 24V DC
5 | Available in multiple tones
6 | Weatherproof housing