## ELEC.-final
PROJECT - BILL OF QUANTITIES FOR ELECTRICAL WORKS (GROUND FLOOR)
BANK - UCO BANK
BRANCH - CHARBAGH
REGION - LUCKNOW
S.NO. | DESCRIPTION OF ITEM | QUANTITY | UNIT | RATE (Rs.) | AMOUNT (Rs.)
1 | ELECTRICAL PANEL (UPGRADATION AS / SPEC. BELOW) Design, manufacture, providing, storing & installing in position, effecting proper connection, testing and commissioning of panel made of 14 SWG, CRCA sheet steel. It shall be dust and vermin proof. It shall have compartmentalized construction with bus bar chambers, cable alley, cable glands plate etc. as required, duly painted from inside as well outside. It shall have the following -
a. | MAIN PANEL 3 Nos. (100 Amp.) Kit Kat switches with neutral links Incoming. 1 No. 100 Amp. TPN, MCCB (10 KA breaking capacity), Busbars. 125 Amp., 3 phase, 4 strips, 415 volts, 50 Hz. copper busbars with colour coded PVC heat shrinkable sleeves. Metering. 1 No. Voltmeter (range 0-500V), 3 phase. 1 No. Ammeter (range 0-200 Amp.), 3 phase with CT operation. 3 Nos. Phase Indication Lamps (red, yellow and blue). Outgoing. 2 Nos. (40 Amp.) TPN, MCCB for UPS DB. and L&F DB 1 No. (63 Amp.) TPN, MCCB for Power DB. 1 No. (80 Amp.) TPN, MCCB for A.C. DB. 1 No., 63 Amp. Three Phase Change Over for D.G. Set. 1 No., 63 Amp. Phase Selector / Rotary for U.P.S. The design of panel should be got approved by the Architect before manufacturing. Also, the provision for 1/2 spare outgoings should be considered for A.T.M. and future expansion. The job shall be completed, to the satisfaction of the Bank Engineer/Architect. | 1 | Job
2 | UPS I/P, O/P AND DISTRIBUTION
a. | 40 AMP. DP MCB with Metal Eclouser for Input & Output | 4 | Nos.
b. | 4 WAY TPN DB (1 No. 40/63 AMP TP MCB and 12 NOS. 6-32 AMP. SPMCB) Horizontal type | 0 | No.
c. | 12 WAY SPN DB (1 No. 40/63 AMP DP MCB and 10 NOS. 6-32 AMP. SPMCB) Horizontal type | 1 | No.
d. | 20 AMP. 3/5 Pin Socket with plate and PVC Box | 4 | Nos.
3 | RAW POWER & FAN, LIGHTING DB & AC DISTRIBUTION BOARD
a. | 4 WAY TPN DB (1 No.63/40/80 AMP. TP MCB and 12 NOS. 6-32 AMP. SPMCB) Horizontal type | 2 | Nos.
b. | 4 WAY TPN DB (1 No. 80 AMP. TP MCB and 12 NOS. 6-32 AMP. SPMCB) Vertical type | 0 | No.
4 | CABLES
a. | Supplying, laying, testing & commissioning of 4 C X 25 sq.mm. at 1100 volts grade PVC insulated aluminum conductor armoured cable with 10 gauge earth copper wire including cables end termination using appropriate Lugs, Glands, termination accessories, Clamps etc. as required as per specification (Mains). | 15 | Mtr.
b. | Supplying, laying, testing & commissioning of 4 C X 10 sq.mm. at 1100 volts grade PVC insulated aluminum conductor armoured cable with 10 gauge earth copper wire including cables end termination using appropriate Lugs, Glands, termination accessories, Clamps etc. as required as per specification (Light & Fan DB, UPS Input). | 45 | Mtr.
c. | Supplying, laying, testing & commissioning of 4 C X 16 sq.mm. at 1100 volts grade PVC insulated aluminum conductor armoured cable with 10 gauge earth copper wire including cables end termination using appropriate Lugs, Glands, termination accessories, Clamps etc. as required as per specification (Power DB) (AC DB) & (GENERATOR). | 25 | Mtr.
5 | AC (SPLIT) POINT
a. | Point Wiring 2 No. 4.0 Sq.mm and 1 No. 2.5 Sq.mm Multistrand Copper Wire. | 60 | Mtr.
b. | 20 AMP. 3/5 Pin Socket with plate and PVC Box | 3 | Nos.
6 | EARTHING
a. | Preparation and commissioning of earth pits with 600x600x3mm thick hot dipped copper electrode with watering arrangement, chamber, funnel, charcoal, salt etc. The electrode shall be connected with 25mmx3mm thick copper strip and terminated into the chamber with nut bolt arrangement. the rate shall inculde cost of earthing strip upto the chamber. Water Funnel with chamber cover | 2 | Nos.
b. | 12 SWG Bare Copper Earth Wire from earthing pit to UPS DB and Main DB | 0 | Mtr.
c. | 6.0 Sq.mm. Cu. Wire from earthing pit to UPS DB and Main DB. Also for A.T.M. & UPS. | 55 | Mtr.
7 | U.P.S. POINT
| Supply & Installation of point wiring for UPS or stabilized power plug points on workstations / table for computers using 3 X1.5 Sq.mm copper conductor multi starnd FR PVC sheathed flexible wire pulled through floor raceways/conduit and taken upto table top using PVC rigid or flexible conduits run within wooden/metal partitions. Each point consisting of 3 nos of 5A , 2/3 pin sockets & 1 No., 15A Switch , wired together forming one point. The earth wire of green color only. | 8 | Nos.
8 | RAW POWER POINT
| Supply & Installation of point wiring for Raw power plug points on workstations / table for computers using 3 X2.5 Sq.mm copper conductor PVC sheathed flexible wire pulled through already laid floor raceways and taken upto table top using PVC rigid or flexible conduits run within wooden/metal partitions. Each point consisting of 1 nos of 16A , 2/3/5 pin sockets & 1 No., 16A Switch , wired together forming one point. The earth wire of green color only. | 7 | Nos.
9 | LIGHT/FAN POINT
Supply & Installation of concealed point wiring using 600v grade 1.5 Sq.mm copper conductor PVC insulated wires (with proper R,Y,B color code ) pulled through heavy gauge PVC conduits laid concealed over false ceiling including 2 Nos. 2.5 sqmm circuit wires from the relevant DB and also including 2.5 sqmm green color copper earth wire and switch plate, switches, etc. Each switch board consisting of 1 nos of 5A , 3/5 pin sockets & 1 No., 5A Switch as approved by the Bank's Engineer/Architect.
a. | Primary light points including the cost of 5A switch | 40 | Nos.
b. | Secondary light points | 10 | Nos.
c. | Ceiling Fan Point including the cost of 5A Switch along with electronic regulator. | 2 | Nos.
10 | DATA CABLING & POINT
Supplying and laying of D-Link make CAT-6 (UTP) cable
a. | Supplying and Installing D-Link make CAT-6 information outlet with plate & surface Box at individual Tables. This work includes supply and laying of CAT-6 cable in PVC conduits throughout the length, from the I/O hub to the point. | 7 | Nos.
b. | Supplying and fixing of 2.0 Mtr long crimped patch cord | 7 | Nos.
b. | Supplying and fixing of 1.0 Mtr long crimped patch cord | 7 | Nos.
c. | Jack Panel - 24 ports | 1 | No.
d. | SITC of 9U Rack including wire manager, power supply card, hardwares etc. complete in all respects | 1 | No.
11 | VOICE NETWORKING
a. | Supply and fixing of 20 pair telephone MDF consisting of tag blocks, disconnector type, complete with powder coated metal enclose, krone tag block mounting arrangement telephone distribution chart and locking arrangement [for P&T/EPABX] | 2 | Jobs
b. | Supplying and laying telephone cables 0.5mm dia electrolytic tinned copper conductors PVC insulated with gel and twisted pair with rip cord, through already laid PVC conduits/Raceways. The rate shall include termination at both ends on tag blocks.
(i) | 10 pair cable | 25 | Mtr.
(ii) | 2 pair cable | 25 | Mtr.
c. | 1 No. RJ11 Telephone socket with plate and box | 1 | No.
12 | FIXTURES
Providing, storing & installing in position, effecting proper connection, testing and commissioning of Light fitting, recessed in false ceiling, with all accessories. The job shall be complete, to the satisfaction of the Bank's Engineer/Architect.
a. | LED 18 W tube 4'-0" As specified in tender document or approved by SBIIMS/Architect. | 4 | No.
b. | Full Glow 2'0" X 2'0" LED 48 W slim Smart Panel of make As specified in tender document or approved by SBIIMS/Architect. | 7 | Nos.
c. | Full Glow 1'0" X 1'0" LED 25 W slim Smart Panel of make As specified in tender document or approved by SBIIMS/Architect. | 0 | Nos.
d. | Full Glow 6" X 6" LED 15 W slim Smart Panel of make As specified in tender document or approved by SBIIMS/Architect. | 16 | Nos.
e. | Full Glow 4" X 4" LED 15 W slim Smart Panel of make As specified in tender document or approved by SBIIMS/Architect. | 0 | Nos.
f. | Bracket Holder with LED Lamp, 7 Watt of make As specified in tender document or approved by SBIIMS/Architect. | 2 | Nos.
g. | Supply, installation, testing and commissioning of following fans with all fixing materials like white Polycarbonate 2 mm Hylem sheet cover, down rods, fan box as required etc. all complete as per the directions of Engineer-in-charge.
(i) | Wall mounted fans (METAL BODY) 400 mm dia. make As specified in tender document or approved by concerned office in charge. | 3 | Nos.
(ii) | Ceiling fans 1200/900 mm dia. make As specified in tender document or approved by concerned office in charge. | 2 | Nos.
(iv) | Supply & fixing of 300 mm exhaust fan 'Ventilair DX W' with self-closing louvers and plastic body with all accessories etc. complete of make As specified in tender document or approved by concerned office in charge. | 2 | Nos.
(iii) | Supply & fixing of 150 mm INLINE exhaust fan for machanical vetilation with all accessories etc. complete of make As specified in tender document or approved by concerned office in charge. | 0 | Nos.
h. | CALL BELL Providing, storing & installing in position, effecting proper connection, testing and commissioning of Call Bell with all accessories. Fixtures - Anchor – City Ding Dong Door Bell. Bell Push - Anchor – Penta, Model – 50042. The job shall be complete, to the satisfaction of the Bank's Engineer/Architect. | 1 | No.
i. | P/F Cove light in false ceiling of make As specified in tender document or approved by SBIIMS/Architect. | 10 | Mtr.
13 | DISTRIBUTION BOARD FOR A.T.M./E-LOBBY
a. | 4 WAY TPN DB (1 No. 63 AMP. MCCB and 12 NOS. 6-32 AMP. SPMCB) Horizontal type | 0 | Job
Total Tendered Cost = (B) (Rs.)
Less - Discount (Rs.)
Balance (Rs.)
Add - Goods & Services Tax (CGST) (Rs.)
Add - Goods & Services Tax (SGST) (Rs.)
Add - Transportation / Cartage (Rs.)
Net Amount (Rs.)
Amount in words -
Rupees _____________________________________________
____________________________________________________ .
(Signature & Seal of Electrical Contractor)