## Estimate Branch
B.O.Q FOR ELECTRICAL WORK FOR UCO BANK, BHANDARIPOKHARI BRANCH.
SL.NO. | DESCRIPTION OF ITEMS | UNIT | QUANTITY | RATE | AMOUNT
1.1 ELECTRICAL WIRING WORK
1 | Concealed / Ressessed / Surface point etc. wiring using 1100V FRLS grade 3R (P+N+E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling, with modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make. S.I.T.C.( Supply Installation Testing And Commissioning) as directed by the Engineer-in-charge. (Each circuit shall not feed more than 8 points OR 800 watts as per following configuration.)
NOTE:- 1. Only FRLS wire shall be used; 2. The wires from ceiling junction to light points / light fixture shall be drawn in flexible PVC conduit with adptor & cover for junction box & crimp type lugs at both the ends alongwith necessary hardware & accessories, etc. as required; 4. Looping of Neutral / Earth wire between two seperate Primary / Full Points is strictly not allowed; 5. Looping of Neutral / Earth wire between two seperate circuits on similar or other phase is strictly not allowed; 6. Ferulling / numbering / taggning to wires with circuit number & db name for all lighting & raw / ups power shall be strictly followed at both DB & switch board / switch socket boards ends.
1.1 | Primary light/Call bell points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make. S.I.T.C. as directed by the Engineer-in-charge.( 1 light controlled by one switch) | Nos. | 24
1.2 | Primary Fan points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make. S.I.T.C. as directed by the Engineer-in-charge.( 1 fan controlled by one switch) | Nos. | 2
1.3 | Subsequent point ( Looped From Primary) | Nos | 14
1.4 | Independent point using one 6 Amp Modular Switch and one 6 Amp, 2/3 pin Modular scoket mounted on a sutable size Box for wall fans. | Nos | 10
1.5 | 6 Amp 2/3 pin Modular scoket with 6A Modular switch. ( on common switch Board.) | Nos. | 3
1.6 | Primary light points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make & model as approved by project in charge. ( I light controlled by one switch UPS point ) | Nos. | 3
2 | Concealed power point using 16 Amp 3 Pin plug socket with 16 Amp Modular switch of legrand mylinc or equivalent make mounted on separate board using suitable size galvanized iron junction & switch boxes & clip in type modular type switch plate,etc. Supply taken from R.D.B./ Nearest L.D.B wiring using 1100V FRLS grade 2R (P+N) x 2.5 Sq.mm +1R (E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick . The point should not taken from any switch Board. S.I.T.C. as directed by the Engineer-in-charge. | Nos | 2
3 | Concealed raw power point using 6 Amp, 2/3 Pin Modular plug socket with 6 Amp Modular switch of legrand mylinc or equivalent make on separate board using galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI/PVC concealed back box, etc. Supply taken from Nearest L.D.B.wiring using 1100V FRLS grade 2R (P+N) x 2.5 Sq.mm +1R (E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick. Maximun 3 Points per Circuit for counter & Table | Nos | 7
4 | Supply,installation and testing of timer with contactor ( L&T / Legrand ) make controlling the glowsign board with 16 Amp Modular switch of legrand mylinc or equivalent make mounted on separate board using suitable size galvanized iron junction & switch boxes & clip in type modular type switch plate,etc all accessories complete enclosed in Powder coated metal box as required,Supply taken from Nearest L.D.B.wiring using 1100V FRLS grade 2R (P+N) x 2.5 Sq.mm +1R (E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick as per direction of Engineer in charge. The system will be apart of the panel board. | Nos. | 1
5 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade multi standard FRLS copper wire run inside rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
5.1 | Recessed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( LDB/RDB to Common Switch board and Points) | Mts | 95
5.2 | Recessed wiring with ( 4Rx10sqmm + 2Rx6sqmm) copper wire ( PANEL to U.P.S. input ) | Mts | 15
TOTAL FOR ELECTRICAL WIRING WORK
1.2 A.C. WIRING WORK
1 | Supply & Installation of all required materials and wiring to Split AC point 25 Amp 3 Pin Modulat socket mouted on suitable size concealed GI Box near to the AC controlled by 25 Amp DP isolator Enclosed in Powder coated DP Encloser of Legrand Ekinox3 model or Equivalent make taken from Nearest A.C..D.B/ M.L.D.B. with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make.The point should not taken from any switch Board S.I.T.C. as directed by the Engineer-in-charge. | Nos. | 4
2 | Supply and Installation of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade standard FRLS copper wire run through rigid FR/FRLS PVC conduits of 20mm/32mm Dia 1.5 mm thick ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
2.1 | Concealed wiring with 2 X 4sq. mm + 1 X 2.5sqmm copper wire ( From Main Panel Board to Split A.C. points. ) | Mts | 80
| TOTAL FOR AC WIRING WORK |  |  | Rs.
1.3 COMPUTER WIRING WORK
1 | Supplt and fixing of concealed UPS power points using 1 nos. of 16 Amp, Modular switches to be provided on table top + 4 nos. 6 Amp 3 Pin Modular socket below table top of legrand mylinc or equivalent make taken from Nearest C.D.B with sutable size galvanized iron/PVC junction & switch boxes & clip in type modular type switch plate, GI/PVC concealed back box, etc. Maximun 3 Points per Circuit for counter & Table. S.I.T.C. as directed by the Engineer-in-charge. | SET | 7
2 | Supplt and fixing of concealed UPS power points using clip in modular type 5 No. of 6/16 amp socket points controlled by 2 No of 16 amp modular switch with indicator of legrand mylinc or equivalent make taken from Nearest C.D.B with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed black box, etc. . The point should not from any switch Board S.I.T.C. as directed by the Engineer-in-charge. | SET | 1
3 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated1100V FRLS grade 3R (P+N+E) x folling size FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick ISI mark laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling including of as required and multy stranded copper wire of folling size as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
3.1 | Concealed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( C.D.B. to Computer Points ) | Mts | 110
3.2 | Concealed wiring with ( 2Rx4.0 sqmm +1Rx2.5sqmm) copper wire ( U.P.S. OUTPUT to C.D.B. ) | Mts | 10
| TOTAL FOR COMPUTER WIRING WORK |  |  | Rs.
2.PANEL BOARD & DISTRIBUTION BOARDS.
1 | Main Panel Board | Set | 1
Supply, delivery, installation , testing , commissioning , of indoor wall mounted , type distribution boards made out of 2 mm thk. CR sheet metal painted with 2 coats of enamel paint compartment arrangement for each equipment & bus bar chamber on the top of the panel running horizontal through , vermin proof having provision cable by conduit entry , earthling stud as per specification mentioned below duly factory wired confirming to the relevant ISS & as per special condition of contract , making good the damages M.S. Cubical type Panel board should have hinged door at the front. The panel shall be provided with all accessories & following arrangements complete in all respect & direction of EIC (before fabrication of panel board drawing is to be approved by Engineer-in-charge). The Contractor should Submit The Testing Cartificate to the Client after Installation.
Incoming :-
1No 125A- 25KA - 4POLE -MCCB.
1 set of 125A TPN copper bus bar (18 X6 mm)
1No 63A- 10KA - 4POLE -MCB.
1 set of 100A TPN copper bus bar(16 X 5 mm)
63A, 4-POLE Change over
1 set of 100 A TPN copper bus bar(16 X 5 mm)
Out going :-
1 Nos 40A, 4P MCB, for U.P.S.
1 Nos 40A, 4P MCB, Spare
1 Nos 32 A DP MCB for L.D.B.
1 Nos 32 A DP MCB for ATM
4 Nos 25 A DP MCB for AC
1 Nos 25 A DP MCB for Glow sign board & Outer Lighting
2 Nos 25 A DP MCB Spare
1 Nos 32 A DP MCB Spare
All MCB must be class C Type
1No. Digital Volt meter with Volt meter selector switch & Control fuse.
1No. Digital Ammeter with Ammeter selector switch & CT.
Cable tray.
Termination bar for each out put
6 Nos Phase indicator L.E.D. lamps
2 | Supplying & Fixing 100 Amp, 415 V Wireable IC Cutout - 3nos in MS enclouser withj lock & key arrangements. | Set | 1
3 | Supply and installation of SPN, Double Door, Metal type Distribution Board. (hager IP43, legrand make Ekinox3 model or equivalent make as approved by Engineer-in-charge ), surface / flush mounted on wall, interconnected wiring complete with earthing lugs, including DB wiring, termination of circuits with ping type copper lugs, blank plates, etc. housing following switchgears :
3.1 | L.D.B (Light Distribution Board) | Set | 1
12 way SPN DB
Incoming :- 1 No. 32A DP MCB
Outgoing :- 10 No. 6-10 A SP MCB
All MCB must be 'C' Series
3.2 | C.D.B (Computer Distribution Board) | SET | 1
12 way SPN DB
Incoming :- 1 No. 32A DP MCB
Outgoing :- 10 No. 6-10 A SP MCB
All MCB must be 'C' Series
3.3 | U.P.S Incoming DB | SET | 1
4 way SPN DB
40 Amp DP-10 kA - MCB – 2 nos (1main & 1 spare).
All MCB must be class C Type
3.4 | U.P.S Outgoing DB | SET | 1
4 way SPN DB
Incoming :- 40 Amp DP-10 kA - MCB – 1 No
Out going :- 2 No. 25 A SP-10 kA - MCB
All MCB must be class C Type
| TOTAL FOR PANEL BOARD & DISTRIBUTION BOARDS. |  |  | Rs.
3. FITTINGS OF FIXTURES
(NOTE : ANY OF FIXTURES AND FITINGS SHALL BE RE-CONFIRMED WITH THE ARCHITECTS / CONSULANTS BEFOTE ORDERING THEM.
Supply , Installation, testing and commissioning of lighting fixtures with lamps and LED driver as per the details below including necessary hardware such as clamps, nuts, bolts, nails, screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant / client including supply and fixing flexible wires from holder to fixtures hardwares etc. Note :- All Light Fixtures, Fans, Exhaust Fans & other fittings samples shall be approved by the Client / Architect / Consultant before placing order to the Light Fixture Vendor / Supplier makes are specified. Client / Architect / Consultant reserves right to approve / select final Light Fitxtures from any make as required.
1 | Supply,installation and testing of recess LED lights fittings ( 31 - 34 W) of squre type ( 2'-0"x2'-0") with all accessories complete of Crompton LCTLRN-36-FO-CDL Equivalent Make as required as per direction of Engineer in charge. | Nos. | 8
2 | Supply,installation and testing of recess LED lights fittings (12W) of spot type with all accessories complete of Crompton LSCRM-6W-CDL/NW/WW Equivalent Make as required as per direction of Engineer in charge. | Nos. | 18
3 | Providing and fitting of 400 mm sweep High Flo Wall fan of Orient/ Crompton Equivalent Make as required as per direction of Engineer in charge. | Nos. | 10
4 | Providing and fitting of 225 mm sweep heavy duty Exhust fan of Orient/ Crompton Equivalent Make as required as per direction of Engineer in charge. | Nos. | 3
5 | Providing and fitting of 1200 mm sweep celing fan of Orient/ Crompton High Speed Equivalent Make as required as per direction of Engineer in charge. | Nos. | 2
6 | Providing and fitting of Modular type step fan regulator of approved make . | Nos. | 2
7 | Supply & fixing of fan-hook,by cutting roof slab and welding 10 mm dia.Fan hook with main re-Inforcemerit of roof slab complete in all respect | Nos. | 2
8 | Supplying , fixing of 1x 20W LED Batten lights fittings with aall accessories complete of Philips BN021C LED20S PSU CDL/NW GR Equivalent Make as required as per direction of Engineer in charge. | Nos. | 5
9 | Supply,installation and testing of LED Bulb fittings (1x9wt) with angle holder of Philips/ Crompton/ Syska or equivelent as required as per direction of Engineer in charge. | Nos | 4
10 | Providing and fitting of call bell Remote Controlled with Battery of approved make . | Nos. | 1
| TOTAL FOR FITTINGS OF FIXTURES |  |  | Rs.
4. EARTHING
1 | Supplying and fixing Earthing with G.I. earth plate of size 600 mm X 600 mm X 6.36 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with alternative layer of 150mm thick charcoal/ coke and salt as required. | Nos. | 2
2 | Supplying and fixing of Earthing with copper earth plate of size 600 mm X 600 mm X 3.18 mm thick including accessories, and providing masonry enclosurewith cover plate having locking arrangement and watering pipeof 2.7 metre long etc. with alternative layer of 150mm thick charcoal/ coke and salt as required. | SET | 1
3 | Supplying and laying 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | Mts | 6
4 | Supplying and laying 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Mts | 20
5 | Supplying and laying earth connection from earth electrode with 4.00 mm dia copper wire in 15 mm dia G.I. pipe from earth electrode including connection with copper thimble excavation and re-filling as required. | Mts. | 3
6 | Supplying and laying 4.00 mm dia copper wire on surface or in recess for loop earthing as required. | Mts. | 10
| TOTAL EARTHING |  |  | Rs.
5.DATA / TELEPHONE WAIRING
1 | Supply of all required materials and laying of CAT-6 LAN wairing from server to Hub and Hub to computer I/O Points of approved brand ((D-Link/Digilink/Amps ) laid through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. or to be cleated on wall / ceiling with saddles / spacer etc. necessary termination etc. completeas in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge. | Mts | 130
2 | Supply of all required materials & laying 2 pairs 0.51 cross section telephone wires of ITI approved laid through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. or to be cleated on wall / ceiling with saddles / spacer etc. necessary termination etc. completeas in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge. | Mtrs. | 50
3 | Supply , fixing of RJ 45 information outlet (I/O) with safey sutter of D-link make with front modular cover plate, flush box metallic or PVC for trucking system etc. | Nos. | 8
4 | Supply , fixing , testing of RJ11 Modular Telephone socket point with suitable GI boxes complete in all respect as per direction of EIC . | Nos. | 3
5 | Supply & fixing 9'' 9 U wall mounted modem rack with power distribution box,cable manager, cantilever self, fan & mounting kit etc all complete.( Make Valrack, Comrack, HCL ) | Set | 1
6 | Supply & fixing 24 port PATCH PANEL ( Make D-LINK, AMP, HCL ) | No | 1
7 | Supply and fixing 24 port - 10/100/1000 mbps- L2 unmanaged switch with 2SFP port. (Giga switch) of ( Cisco / D-link / Zyxel/ HP ) | Nos. | 1
8 | Supply & fixing 1Mtr long E-CAT 6 PATCH Cord (Make D-LINK,AMPor Equivalent Make) | No. | 8
9 | Supply & fixing 2Mtr long E-CAT 6 PATCH Cord (Make D-LINK,AMP or Equivalent Make) | No. | 8
| TOTAL DATA / TELEPHONE WAIRING |  |  | Rs.
1.1 ELECTRICAL WIRING WORK
1.2 A.C. WIRING WORK
1.3 COMPUTER WIRING WORK
2.PANEL BOARD & DISTRIBUTION BOARDS.
3. FITTINGS OF FIXTURES
4. EARTHING
5.DATA / TELEPHONE WAIRING
TOTAL

## Estimate ATM
B.O.Q FOR ELECTRICAL WORK FOR UCO BANK ATM AT BHANDARIPOKHARI.
SL.NO. | DESCRIPTION OF ITEMS | UNIT | QUANTITY | RATE | AMOUNT
1.1 ELECTRICAL WIRING WORK
1 | Concealed / Ressessed / Surface point etc. wiring using 1100V FRLS grade 3R (P+N+E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling, with modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make. S.I.T.C.( Supply Installation Testing And Commissioning) as directed by the Engineer-in-charge. (Each circuit shall not feed more than 8 points OR 800 watts as per following configuration.)
NOTE:- 1. Only FRLS wire shall be used; 2. The wires from ceiling junction to light points / light fixture shall be drawn in flexible PVC conduit with adptor & cover for junction box & crimp type lugs at both the ends alongwith necessary hardware & accessories, etc. as required; 4. Looping of Neutral / Earth wire between two seperate Primary / Full Points is strictly not allowed; 5. Looping of Neutral / Earth wire between two seperate circuits on similar or other phase is strictly not allowed; 6. Ferulling / numbering / taggning to wires with circuit number & db name for all lighting & raw / ups power shall be strictly followed at both DB & switch board / switch socket boards ends.
1.1 | Primary light points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make & model as approved by project in charge. ( I light controlled by one switch UPS point ) | Nos. | 3
1.2 | Subsequent point ( Looped From Primary) | Nos | 3
2 | Supply,installation and testing of timer with contactor ( L&T / Legrand ) make controlling the glowsign board with 16 Amp Modular switch of legrand mylinc or equivalent make mounted on separate board using suitable size galvanized iron junction & switch boxes & clip in type modular type switch plate,etc all accessories complete enclosed in Powder coated metal box as required,Supply taken from Nearest L.D.B.wiring using 1100V FRLS grade 2R (P+N) x 2.5 Sq.mm +1R (E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick as per direction of Engineer in charge. The system will be apart of the panel board. | Nos. | 1
3 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade multi standard FRLS copper wire run inside rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
3.1 | Recessed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( LDB/RDB to Common Switch board and Points) | Mts | 20
3.2 | Recessed wiring with ( 2Rx4sqmm +1Rx2.5sqmm) copper wire ( Panel to ATM) | Mts | 10
| TOTAL FOR ELECTRICAL WIRING WORK |  |  | Rs.
1.2 A.C. WIRING WORK
1 | Supply & Installation of all required materials and wiring to Split AC point 25 Amp 3 Pin Modulat socket mouted on suitable size concealed GI Box near to the AC controlled by 25 Amp DP isolator Enclosed in Powder coated DP Encloser of Legrand Ekinox3 model or Equivalent make taken from Nearest A.C..D.B/ M.L.D.B. with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make.The point should not taken from any switch Board S.I.T.C. as directed by the Engineer-in-charge. | Nos. | 2
2 | Supply and Installation of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade standard FRLS copper wire run through rigid FR/FRLS PVC conduits of 20mm/32mm Dia 1.5 mm thick ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
2.1 | Concealed wiring with 2 X 4sq. mm + 1 X 2.5sqmm copper wire ( From Main Panel Board to Split A.C. points. ) | Mts | 2
| TOTAL FOR AC WIRING WORK |  |  | Rs.
1.3 COMPUTER WIRING WORK
1 | Concealed power point using 16 Amp 3 Pin plug socket with 16 Amp Modular switch of legrand mylinc or equivalent make mounted on separate board using suitable size galvanized iron junction & switch boxes & clip in type modular type switch plate,etc. Supply taken from R.D.B./ Nearest L.D.B wiring using 1100V FRLS grade 2R (P+N) x 2.5 Sq.mm +1R (E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick . The point should not taken from any switch Board. S.I.T.C. as directed by the Engineer-in-charge. | Nos | 4
2 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated1100V FRLS grade 3R (P+N+E) x folling size FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick ISI mark laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling including of as required and multy stranded copper wire of folling size as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
2.1 | Concealed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( C.D.B. to Computer Points ) | Mts | 20
| TOTAL FOR COMPUTER WIRING WORK |  |  | Rs.
2. FITTINGS OF FIXTURES
(NOTE : ANY OF FIXTURES AND FITINGS SHALL BE RE-CONFIRMED WITH THE ARCHITECTS / CONSULANTS BEFOTE ORDERING THEM.
Supply , Installation, testing and commissioning of lighting fixtures with lamps and LED driver as per the details below including necessary hardware such as clamps, nuts, bolts, nails, screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant / client including supply and fixing flexible wires from holder to fixtures hardwares etc. Note :- All Light Fixtures, Fans, Exhaust Fans & other fittings samples shall be approved by the Client / Architect / Consultant before placing order to the Light Fixture Vendor / Supplier makes are specified. Client / Architect / Consultant reserves right to approve / select final Light Fitxtures from any make as required.
1 | Supply,installation and testing of recess LED lights fittings (18W) of squre type with all accessories complete Crompton LSDN-18-CDL/TL/WW Equivalent Make as required as per direction of Engineer in charge. | Nos. | 2
2 | Supply,installation and testing of recess LED lights fittings (12W) of spot type with all accessories complete of Crompton LSCRM-6W-CDL/NW/WW Equivalent Make as required as per direction of Engineer in charge. | Nos. | 4
| TOTAL FOR FITTINGS OF FIXTURES |  |  | Rs.
4.DATA / TELEPHONE WAIRING
1 | Supply of all required materials and laying of CAT-6 LAN wairing from server to Hub and Hub to computer I/O Points of approved brand ((D-Link/Digilink/Amps ) laid through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. or to be cleated on wall / ceiling with saddles / spacer etc. necessary termination etc. completeas in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge. | Mts | 50
2 | Supply , fixing of RJ 45 information outlet (I/O) with safey sutter of D-link make with front modular cover plate, flush box metallic or PVC for trucking system etc. | Nos. | 4
3 | Supply & fixing 1Mtr long E-CAT 6 PATCH Cord (Make D-LINK,AMPor Equivalent Make) | No. | 4
4 | Supply & fixing 2Mtr long E-CAT 6 PATCH Cord (Make D-LINK,AMP or Equivalent Make) | No. | 4
| TOTAL DATA / TELEPHONE WAIRING |  |  | Rs.
1.1 ELECTRICAL WIRING WORK
1.2 A.C. WIRING WORK
1.3 COMPUTER WIRING WORK
2. FITTINGS OF FIXTURES
3.DATA / TELEPHONE WAIRING
TOTAL

## Analysis (hidden)
ANALYSIS OF RATES FOR ELETRICAL WORK
SL NO | DESCRIPTION OF ITEM | QTY | UNIT | Rate in Rs. | Rate/ Unit | Quantity required | Amount in Rs.
Recessed wiring to light point
A1 | A1 materials
1 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X3 = 9 + 0.45 (wastage @ 5%) =9.45m | 90 | Mtr | 928.2 | 10.3133 | 9.45 | 97.461
2 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
3 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
4 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
6 | Modular GI box for 2module 18 swg | 1 | Nos | 22.5 | 22.5 | 1 | 22.5
7 | Modular base & cover plate for 2 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
8 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 1 | 62.4
9 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
10 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
11 | Total A1 | [5 empty] | 266.435
A2 | Cartage 1% of A1 | [5 empty] | 2.6644
| Wastage 1% of A1 | [5 empty] | 2.6644
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 2.6644
| TOTAl A2 | [5 empty] | 7.9931
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 315.9
| (A1+A2+A3) | [5 empty] | 590.328
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 14.7582
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 73.791
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 678.8773
[6 empty] | ORSAY | 679
Recessed wiring to FAN point
A1 | A1 materials
1 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X3 = 9 + 0.45 (wastage @ 5%) =9.45m | 90 | Mtr | 928.2 | 10.3133 | 9.45 | 97.461
2 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
3 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
4 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
6 | Modular GI box for 2module 18 swg | 1 | Nos | 22.5 | 22.5 | 1 | 22.5
7 | Modular base & cover plate for 2 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
8 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 1 | 62.4
9 | Ceilling rose 5amp, 250 V ISI marked | 1 | Nos | 22 | 22 | 1 | 22
10 | 3 mm thick phenolic laminated sheet | 1 | sqcm | 0.2 | 0.2 | 50 | 10
11 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 6 | 1.8
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.2 | 6
| Total A1 | [5 empty] | 300.035
A2 | Cartage 1% of A1 | [5 empty] | 3.0004
| Wastage 1% of A1 | [5 empty] | 3.0004
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.0004
| TOTAl A2 | [5 empty] | 9.001
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.125 | 65.875
| Khallasi | 1 | Day | 466 | 466 | 0.325 | 151.45
| Total A3 | [5 empty] | 340.725
| (A1+A2+A3) | [5 empty] | 649.761
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 16.244
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 81.2201
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 747.2252
[6 empty] | ORSAY | 747
Subsequent point
A1 | A1 materials
1 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X3 = 9 + 0.45 (wastage @ 5%) =9.45m | 90 | Mtr | 928.2 | 10.3133 | 9.45 | 97.461
2 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
3 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
4 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 0.25 | 1.25
| Total A1 | [5 empty] | 139.135
A2 | Cartage 1% of A1 | [5 empty] | 1.3914
| Wastage 1% of A1 | [5 empty] | 1.3914
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 1.3914
| TOTAl A2 | [5 empty] | 4.1741
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.1 | 61.7
| Masson Grade II | 1 | Day | 527 | 527 | 0.05 | 26.35
| Khallasi | 1 | Day | 466 | 466 | 0.1 | 46.6
| Total A3 | [5 empty] | 134.65
| (A1+A2+A3) | [5 empty] | 277.959
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 6.949
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 34.7449
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 319.6529
[6 empty] | ORSAY | 320
WALL FAN point
A1 | A1 materials
1 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X3 = 9 + 0.45 (wastage @ 5%) =9.45m | 90 | Mtr | 928.2 | 10.3133 | 9.45 | 97.461
2 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
3 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
4 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
6 | Modular GI box for 3module 18 swg | 1 | Nos | 30.5 | 30.5 | 1 | 30.5
7 | Modular base & cover plate for 3 module | 1 | Nos | 47.95 | 47.95 | 1 | 47.95
8 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 1 | 62.4
9 | 2/3 pin 6 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 1 | 78
10 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
11 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.2 | 6
| Total A1 | [5 empty] | 363.935
A2 | Cartage 1% of A1 | [5 empty] | 3.6393
| Wastage 1% of A1 | [5 empty] | 3.6393
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.6393
| TOTAl A2 | [5 empty] | 10.918
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.25 | 116.5
| Total A3 | [5 empty] | 292.6
| (A1+A2+A3) | [5 empty] | 667.453
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 16.6863
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 83.4316
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 767.571
[6 empty] | ORSAY | 768
6 Amp 2/3 pin Modular scoket with 6A Modular switch. ( on common switch Board.)
A1 | A1 materials
1 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 0.15X3 = 0.45 + 0.04 (wastage @ 5%) =0.49m | 90 | Mtr | 928.2 | 10.3133 | 0.49 | 5.0535
2 | Modular GI box for 3 module 18 swg | 1 | Nos | 30.5 | 30.5 | 1 | 30.5
3 | Modular base & cover plate for 3 module | 1 | Nos | 47.95 | 47.95 | 1 | 47.95
4 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 1 | 62.4
5 | 2/3 pin 6 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 1 | 78
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.2 | 6
| Total A1 | [5 empty] | 229.9035
A2 | Cartage 1% of A1 | [5 empty] | 2.299
| Wastage 1% of A1 | [5 empty] | 2.299
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 2.299
| TOTAl A2 | [5 empty] | 6.8971
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.125 | 77.125
| Masson Grade II | 1 | Day | 527 | 527 | 0.075 | 39.525
| Khallasi | 1 | Day | 466 | 466 | 0.1 | 46.6
| Total A3 | [5 empty] | 163.25
| (A1+A2+A3) | [5 empty] | 400.0506
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 10.0013
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 50.0063
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 460.0582
[6 empty] | ORSAY | 460
Power point using 16 Amp 3 Pin plug socket with 16 Amp Modular switch ( on separate board ).
A1 | A1 materials
1 | 2.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X2 = 6 + 0.3 (wastage @ 5%) =6.3m | 90 | Mtr | 1485.6 | 16.5067 | 6.3 | 103.992
2 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X1 = 3 + 0.15 (wastage @ 5%) =3.15m | 90 | Mtr | 928.2 | 10.3133 | 3.15 | 32.487
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
5 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
6 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
7 | Modular GI box for 3 module 18 swg | 1 | Nos | 30.5 | 30.5 | 1 | 30.5
8 | Modular base & cover plate for 3 module | 1 | Nos | 47.95 | 47.95 | 1 | 47.95
9 | Single Pole 16 amps one way modular switch ISI marked | 1 | Nos | 104.4 | 104.4 | 1 | 104.4
10 | 6 pin 15/16 amps modular socket outlet, ISI marked | 1 | Nos | 123 | 123 | 1 | 123
11 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.2 | 6
| Total A1 | [5 empty] | 489.953
A2 | Cartage 1% of A1 | [5 empty] | 4.8995
| Wastage 1% of A1 | [5 empty] | 4.8995
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 4.8995
| TOTAl A2 | [5 empty] | 14.6986
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 342.25
| (A1+A2+A3) | [5 empty] | 846.9016
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 21.1725
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 105.8627
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 973.9368
[6 empty] | ORSAY | 974
Power point using 2 nos of 6 Amp 2/3 Pin Modular plug socket with 2 nos of 6 Amp Modular switch ( on separate board ).
A1 | A1 materials
1 | 2.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X2 = 6 + 0.3 (wastage @ 5%) =6.3m | 90 | Mtr | 1485.6 | 16.5067 | 6.3 | 103.992
2 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X1 = 3 + 0.15 (wastage @ 5%) =3.15m | 90 | Mtr | 928.2 | 10.3133 | 3.15 | 32.487
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 2.5 + 0.13 (wastage @ 5%) = 2.63m | 3 | Mtr | 32.4 | 10.8 | 2.63 | 28.404
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
5 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
6 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 28 | 28 | 4 | 112
7 | Modular GI box for 6 module 18 swg | 1 | Nos | 50.5 | 50.5 | 1 | 50.5
8 | Modular base & cover plate for 6 module | 1 | Nos | 54.25 | 54.25 | 1 | 54.25
9 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 2 | 124.8
10 | 2/3 pin 6 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 2 | 156
11 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 6 | 1.8
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.4 | 7
| Total A1 | [5 empty] | 677.253
A2 | Cartage 1% of A1 | [5 empty] | 6.7725
| Wastage 1% of A1 | [5 empty] | 6.7725
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 6.7725
| TOTAl A2 | [5 empty] | 20.3176
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.225 | 138.825
| Masson Grade II | 1 | Day | 527 | 527 | 0.125 | 65.875
| Khallasi | 1 | Day | 466 | 466 | 0.35 | 163.1
| Total A3 | [5 empty] | 367.8
| (A1+A2+A3) | [5 empty] | 1065.3706
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 26.6343
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 133.1713
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1225.1762
[6 empty] | ORSAY | 1225
Power point using 6 Amp 2/3 Pin Modular plug socket with 2 nos of 6 Amp Modular switch. ( on separate board ).
A1 | A1 materials
1 | 2.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X2 = 6 + 0.3 (wastage @ 5%) =6.3 m | 90 | Mtr | 1485.6 | 16.5067 | 6.3 | 103.992
2 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 3X1 = 3 + 0.15 (wastage @ 5%) =3.15m | 90 | Mtr | 928.2 | 10.3133 | 3.15 | 32.487
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 0.85 + 0.04 (wastage @ 5%) = 0.89m | 3 | Mtr | 32.4 | 10.8 | 0.89 | 9.612
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
5 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 0 | 0
6 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 2 | 3
7 | Modular GI box for 3 module 18 swg | 1 | Nos | 30.5 | 30.5 | 1 | 30.5
8 | Modular base & cover plate for 3 module | 1 | Nos | 47.95 | 47.95 | 1 | 47.95
9 | Single Pole 6 amps one way modular switch ISI marked | 1 | Nos | 62.4 | 62.4 | 1 | 62.4
10 | 2/3 pin 6 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 1 | 78
11 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.4 | 7
| Total A1 | [5 empty] | 382.161
A2 | Cartage 1% of A1 | [5 empty] | 3.8216
| Wastage 1% of A1 | [5 empty] | 3.8216
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.8216
| TOTAl A2 | [5 empty] | 11.4648
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 315.9
| (A1+A2+A3) | [5 empty] | 709.5258
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 17.7381
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 88.6907
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 815.9547
[6 empty] | ORSAY | 816
Timer with contactor ( L&T / Legrand ) make controlling the glowsign board.
A1 | A1 materials
1 | 2.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 5X2 = 10 + 0.5 (wastage @ 5%) =10.5m | 90 | Mtr | 1485.6 | 16.5067 | 10.5 | 173.32
2 | 1.5sq.mm FRLS PVC insulated single core multistrand copper conductor. = 5X1 = 5 + 0.25 (wastage @ 5%) =5.25m | 90 | Mtr | 928.2 | 10.3133 | 5.25 | 54.145
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 4.8 + 0.24 (wastage @ 5%) = 5.04m | 3 | Mtr | 32.4 | 10.8 | 5.04 | 54.432
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 4 | 24.08
5 | 20 mm PVC Couplers | 1 | Nos | 8.68 | 8.68 | 0 | 0
6 | Two Pole 40A Contactor | 1 | Nos | 784 | 784 | 1 | 784
7 | Digital Time Switch 110 - 240 VAC 1 C/O Base/DIN 16 Pulse | 1 | Nos | 1516 | 1516 | 1 | 1516
8 | Modular GI box for 2 module 18 swg | 1 | Nos | 22.5 | 22.5 | 1 | 22.5
9 | Modular base & cover plate for 1 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
10 | Single Pole 16 amps one way modular switch ISI marked | 1 | Nos | 104.4 | 104.4 | 1 | 104.4
11 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 6 | 9
12 | FP Metal enclosures | 1 | Nos | 480 | 480 | 1 | 480
13 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 8 | 2.4
14 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2.5 | 12.5
| Total A1 | [5 empty] | 3274.227
A2 | Cartage 1% of A1 | [5 empty] | 32.7423
| Wastage 1% of A1 | [5 empty] | 32.7423
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 32.7423
| TOTAl A2 | [5 empty] | 98.2268
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.5 | 308.5
| Masson Grade II | 1 | Day | 527 | 527 | 0.2 | 105.4
| Khallasi | 1 | Day | 466 | 466 | 0.6 | 279.6
| Total A3 | [5 empty] | 693.5
| (A1+A2+A3) | [5 empty] | 4065.9538
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 101.6488
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 508.2442
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 4675.8469
[6 empty] | ORSAY | 4676
Recessed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire
COST FOR 50 METERS
A1 | A1 materials
1 | 2.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 2 = 100 + 5 (wastage @ 5%) =105m | 90 | Mtr | 1485.6 | 16.5067 | 105 | 1733.2
2 | 1.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 90 | Mtr | 928.2 | 10.3133 | 52.5 | 541.45
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 3 | Mtr | 32.4 | 10.8 | 52.5 | 567
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 4 | 24.08
5 | 20 mm PVC Couplers | 1 | Nos | 5.32 | 5.32 | 15 | 79.8
6 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 85 | 127.5
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 85 | 25.5
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 3103.53
A2 | cartage 1% of A1 | [5 empty] | 31.0353
| Wastage 1% of A1 | [5 empty] | 31.0353
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 31.0353
| TOTAl A2 | [5 empty] | 93.1059
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 0.75 | 395.25
| Khallasi | 1 | Day | 466 | 466 | 2.75 | 1281.5
| Total A3 | [5 empty] | 2910.75
| (A1+A2+A3) | [5 empty] | 6107.3859
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 152.6846
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 763.4232
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 7023.4938
A7 | Rate / Mtr=A6/50 | [5 empty] | 140.4699
[6 empty] | ORSAY | 140
Recessed wiring with ( 2Rx4.0sqmm +1Rx2.5sqmm) copper wire
COST FOR 50 METERS
A1 | A1 materials
1 | 4.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 2 = 100 + 5 (wastage @ 5%) =105m | 90 | Mtr | 2226.6 | 24.74 | 105 | 2597.7
2 | 2.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 90 | Mtr | 1485.6 | 16.5067 | 52.5 | 866.6
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 3 | Mtr | 32.4 | 10.8 | 52.5 | 567
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 4 | 24.08
5 | 20 mm PVC Couplers | 1 | Nos | 6.02 | 6.02 | 15 | 90.3
6 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 85 | 127.5
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 85 | 25.5
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 4303.68
A2 | cartage 1% of A1 | [5 empty] | 43.0368
| Wastage 1% of A1 | [5 empty] | 43.0368
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 43.0368
| TOTAl A2 | [5 empty] | 129.1104
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 0.75 | 395.25
| Khallasi | 1 | Day | 466 | 466 | 2.75 | 1281.5
| Total A3 | [5 empty] | 2910.75
| (A1+A2+A3) | [5 empty] | 7343.5404
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 183.5885
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 917.9425
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 8445.0715
A7 | Rate / Mtr=A6/50 | [5 empty] | 168.9014
[6 empty] | ORSAY | 169
Recessed wiring with ( 2Rx6.0 sqmm +1Rx4.0 sqmm ) copper wire
COST FOR 50 METERS
A1 | A1 materials
1 | 6.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 2 = 100 + 5 (wastage @ 5%) =105m | 90 | Mtr | 3315.6 | 36.84 | 105 | 3868.2
2 | 4.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 90 | Mtr | 2226.6 | 24.74 | 52.5 | 1298.85
3 | FRLS PVC conduits of 25 mm Dia 1.5 mm thick. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 3 | Mtr | 42.3 | 14.1 | 52.5 | 740.25
4 | 25mm PVC bends | 1 | Nos | 9.73 | 9.73 | 4 | 38.92
5 | 25 mm PVC Couplers | 1 | Nos | 8.68 | 8.68 | 15 | 130.2
6 | 25 mm iron staples/ saddles/ screws | 1 | Nos | 2.1 | 2.1 | 85 | 178.5
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 85 | 25.5
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 6285.42
A2 | cartage 1% of A1 | [5 empty] | 62.8542
| Wastage 1% of A1 | [5 empty] | 62.8542
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 62.8542
| TOTAl A2 | [5 empty] | 188.5626
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 0.75 | 395.25
| Khallasi | 1 | Day | 466 | 466 | 2.75 | 1281.5
| Total A3 | [5 empty] | 2910.75
| (A1+A2+A3) | [5 empty] | 9384.7326
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 234.6183
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 1173.0916
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 10792.4425
A7 | Rate / Mtr=A6/50 | [5 empty] | 215.8488
[6 empty] | ORSAY | 216
Recessed wiring with ( 4Rx10sqmm + 2Rx6sqmm) copper wire
COST FOR 50 METERS
A1 | A1 materials
1 | 10.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 4 = 200 + 10 (wastage @ 5%) = 210 m | 90 | Mtr | 5838 | 64.8667 | 210 | 13622
2 | 6.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 50 X 2 = 100 + 5 (wastage @ 5%) = 105 m | 90 | Mtr | 3315.6 | 36.84 | 105 | 3868.2
3 | FRLS PVC conduits of 32 mm Dia 1.5 mm thick. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 3 | Mtr | 67.5 | 22.5 | 52.5 | 1181.25
4 | 32 mm PVC bends | 1 | Nos | 26.67 | 26.67 | 4 | 106.68
5 | 32 mm PVC Couplers | 1 | Nos | 12.67 | 12.67 | 15 | 190.05
6 | 32 mm iron staples/ saddles/ screws | 1 | Nos | 3.15 | 3.15 | 85 | 267.75
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 85 | 25.5
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 19266.43
A2 | cartage 1% of A1 | [5 empty] | 192.6643
| Wastage 1% of A1 | [5 empty] | 192.6643
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 192.6643
| TOTAl A2 | [5 empty] | 577.9929
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2.5 | 1542.5
| Masson Grade II | 1 | Day | 527 | 527 | 0.75 | 395.25
| Khallasi | 1 | Day | 466 | 466 | 3.25 | 1514.5
| Total A3 | [5 empty] | 3452.25
| (A1+A2+A3) | [5 empty] | 23296.6729
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 582.4168
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2912.0841
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 26791.1738
A7 | Rate / Mtr=A6/50 | [5 empty] | 535.8235
[6 empty] | ORSAY | 536
Surface wiring with (95sq.mm)3 1/2 core armored almunium cable.
COST FOR 100 METERS
A1 | A1 materials
1 | 95 sq.mm 3 1/2 Core, XLPE Insulated, Aluminum Armoured Cable. = 50 X 4 = 100 + 2 (wastage @ 2%) = 102 m | 1 | Mtr | 360.5 | 360.5 | 102 | 36771
2 | 32mm X 8mm bolts & nuts = 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos | 1 | Nos | 4.3 | 4.3 | 350 | 1505
3 | 25 mm X 3 mm flat iron = 2 x 84 x 0.16m = 26.88m @ 0.674kg/m = 9.06 kg | 1 | kg | 33 | 33 | 9.06 | 298.98
4 | Steel fastener 6 mm X 75 mm | 1 | Nos | 5.5 | 5.5 | 350 | 1925
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2 | 10
| Total A1 | [5 empty] | 40509.98
A2 | cartage 1% of A1 | [5 empty] | 405.0998
| Wastage 1% of A1 | [5 empty] | 405.0998
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 405.0998
| TOTAl A2 | [5 empty] | 1215.2994
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Fitter, Grade II | 1 | Day | 527 | 527 | 1 | 527
| Blacksmith, Grade II | 1 | Day | 527 | 527 | 1 | 527
| Masson Grade II | 1 | Day | 527 | 527 | 1 | 527
| Khallasi | 1 | Day | 466 | 466 | 5 | 2330
| Total A3 | [5 empty] | 5145
| (A1+A2+A3) | [5 empty] | 46870.2794
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 1171.757
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 5858.7849
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 53900.8213
A7 | Rate / Mtr=A6/100 | [5 empty] | 539.0082
[6 empty] | ORSAY | 539
Surface wiring with (35sqmm)3 1/2 core armored almunium cable.
COST FOR 100 METERS
A1 | A1 materials
1 | 35 sq.mm 3 1/2 Core, XLPE Insulated, Aluminum Armoured Cable. = 50 X 4 = 100 + 2 (wastage @ 2%) = 102 m | 1 | Mtr | 169.4 | 169.4 | 102 | 17278.8
2 | GI saddles 19mm x 1 mm = 100/0.45 = 222 + 4 (Wastage @ 2%) = 226 Nos | 1 | Mtr | 1.3 | 1.3 | 226 | 293.8
3 | Iron screws, 45 mm X 6 mm | 1 | Mtr | 1.7 | 1.7 | 452 | 768.4
4 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 452 | 135.6
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2 | 10
| Total A1 | [5 empty] | 18486.6
A2 | cartage 1% of A1 | [5 empty] | 184.866
| Wastage 1% of A1 | [5 empty] | 184.866
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 184.866
| TOTAl A2 | [5 empty] | 554.598
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 1 | 527
| Khallasi | 1 | Day | 466 | 466 | 4 | 1864
| Total A3 | [5 empty] | 3625
| (A1+A2+A3) | [5 empty] | 22666.198
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 566.6549
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2833.2748
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 26066.1277
A7 | Rate / Mtr=A6/100 | [5 empty] | 260.6613
[6 empty] | ORSAY | 261
Surface wiring with 4sq. mm 4 Core, XLPE Insulated, Copper Armoured Cable with 2R X 2.5 sq. mm copper FRLS wire
COST FOR 100 METERS
A1 | A1 materials
1 | 4 sq.mm 4 Core, XLPE Insulated, Copper Armoured Cable. = 100 + 2 (wastage @ 2%) = 102 m | 1 | Mtr | 140.7 | 140.7 | 102 | 14351.4
2 | 2.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. = 100 X 2 = 200 + 4 (wastage @ 2%) =204m | 90 | Mtr | 1485.6 | 16.5067 | 204 | 3367.36
3 | FRLS PVC conduits of 25 mm Dia 1.5 mm thick. = 50 X 1 = 50 + 2.5 (wastage @ 5%) =52.5m | 3 | Mtr | 42.3 | 14.1 | 52.5 | 740.25
4 | 25mm PVC bends | 1 | Nos | 9.73 | 9.73 | 4 | 38.92
5 | 25 mm PVC Couplers | 1 | Nos | 8.68 | 8.68 | 15 | 130.2
6 | 25 mm iron staples/ saddles/ screws | 1 | Nos | 2.1 | 2.1 | 85 | 178.5
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 170 | 51
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2 | 10
| Total A1 | [5 empty] | 18867.63
A2 | cartage 1% of A1 | [5 empty] | 188.6763
| Wastage 1% of A1 | [5 empty] | 188.6763
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 188.6763
| TOTAl A2 | [5 empty] | 566.0289
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2.5 | 1542.5
| Masson Grade II | 1 | Day | 527 | 527 | 1 | 527
| Khallasi | 1 | Day | 466 | 466 | 3.5 | 1631
| Total A3 | [5 empty] | 3700.5
| (A1+A2+A3) | [5 empty] | 23134.1589
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 578.354
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2891.7699
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 26604.2827
A7 | Rate / Mtr=A6/100 | [5 empty] | 266.0428
[6 empty] | ORSAY | 266
Surface wiring with (16sqmm) 4 core armored almunium cable.
COST FOR 100 METERS
A1 | A1 materials
1 | 16 sq.mm 4 Core, XLPE Insulated, Aluminum Armoured Cable. = 100 + 2 (wastage @ 2%) = 102 m | 1 | Mtr | 112.7 | 112.7 | 102 | 11495.4
2 | GI saddles 19mm x 1 mm = 100/0.45 = 222 + 4 (Wastage @ 2%) = 226 Nos | 1 | Mtr | 1.3 | 1.3 | 226 | 293.8
3 | Iron screws, 45 mm X 6 mm | 1 | Mtr | 1.7 | 1.7 | 452 | 768.4
4 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 452 | 135.6
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2 | 10
| Total A1 | [5 empty] | 12703.2
A2 | cartage 1% of A1 | [5 empty] | 127.032
| Wastage 1% of A1 | [5 empty] | 127.032
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 127.032
| TOTAl A2 | [5 empty] | 381.096
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 1 | 527
| Khallasi | 1 | Day | 466 | 466 | 4 | 1864
| Total A3 | [5 empty] | 3625
| (A1+A2+A3) | [5 empty] | 16709.296
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 417.7324
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2088.662
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 19215.6904
A7 | Rate / Mtr=A6/100 | [5 empty] | 192.1569
[6 empty] | ORSAY | 192
Surface wiring with (16sqmm) 4 core armored almunium cable with 2R X 12 SWG GI wire .
COST FOR 100 METERS
A1 | A1 materials
1 | 16 sq.mm 4 Core, XLPE Insulated, Aluminum Armoured Cable. = 100 + 2 (wastage @ 2%) = 102 m | 1 | Mtr | 112.7 | 112.7 | 102 | 11495.4
2 | GI saddles 19mm x 1 mm = 100/0.45 = 222 + 4 (Wastage @ 2%) = 226 Nos | 1 | Mtr | 1.3 | 1.3 | 226 | 293.8
3 | 12 SWG GI Wire = 2 x 100 = 200 + 4 (Wastage @ 2%) = 204 @ 0.044kg/m = 9.06 kg | 1 | kg | 57 | 57 | 8.98 | 511.86
4 | Iron screws, 45 mm X 6 mm | 1 | Mtr | 1.7 | 1.7 | 452 | 768.4
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 452 | 135.6
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 2 | 10
| Total A1 | [5 empty] | 13215.06
A2 | cartage 1% of A1 | [5 empty] | 132.1506
| Wastage 1% of A1 | [5 empty] | 132.1506
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 132.1506
| TOTAl A2 | [5 empty] | 396.4518
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2.25 | 1388.25
| Masson Grade II | 1 | Day | 527 | 527 | 1 | 527
| Khallasi | 1 | Day | 466 | 466 | 4.5 | 2097
| Total A3 | [5 empty] | 4012.25
| (A1+A2+A3) | [5 empty] | 17623.7618
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 440.594
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2202.9702
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 20267.3261
A7 | Rate / Mtr=A6/100 | [5 empty] | 202.6733
[6 empty] | ORSAY | 203
Glanding & Termination for (95sq.mm) 3½ core armored almunium cable .
A1 | A1 materials
1 | Brass compression gland for (45 mm) 3½ X 95 sq. mm 1.1 KV grade cable | 1 | Set | 135 | 135 | 1 | 135
2 | Aluminium lugs for 95 sq. mm cable | 1 | each | 8 | 8 | 3 | 24
3 | Aluminium lugs for 50 sq. mm cable | 1 | each | 4 | 4 | 1 | 4
| Total A1 | [5 empty] | 163
A2 | cartage 1% of A1 | [5 empty] | 1.63
| Wastage 1% of A1 | [5 empty] | 1.63
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 1.63
| TOTAl A2 | [5 empty] | 4.89
A3 | Labour charges
| Cable jointer | 1 | Day | 617 | 617 | 0.16 | 98.72
| Khallasi | 1 | Day | 466 | 466 | 0.16 | 74.56
| Total A3 | [5 empty] | 173.28
| (A1+A2+A3) | [5 empty] | 341.17
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 8.5292
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 42.6463
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 392.3455
[6 empty] | ORSAY | 392
Glanding & Termination for (35sqmm) 3 1/2 core armored almunium cable .
A1 | A1 materials
1 | Brass compression gland for (32 mm) 3½ X 35 sq. mm 1.1 KV grade cable | 1 | Set | 70 | 70 | 1 | 70
2 | Aluminium lugs for 35 sq. mm cable | 1 | each | 3 | 3 | 3 | 9
3 | Aluminium lugs for 25 sq. mm cable | 1 | each | 2 | 2 | 1 | 2
| Total A1 | [5 empty] | 81
A2 | cartage 1% of A1 | [5 empty] | 0.81
| Wastage 1% of A1 | [5 empty] | 0.81
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 0.81
| TOTAl A2 | [5 empty] | 2.43
A3 | Labour charges
| Cable jointer | 1 | Day | 617 | 617 | 0.12 | 74.04
| Khallasi | 1 | Day | 466 | 466 | 0.12 | 55.92
| Total A3 | [5 empty] | 129.96
| (A1+A2+A3) | [5 empty] | 213.39
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 5.3347
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 26.6737
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 245.3985
[6 empty] | ORSAY | 245
Glanding & Termination for (16 sqmm) 4 core armored almunium cable .
A1 | A1 materials
1 | Brass compression gland for (28 mm) 4 X 16 sq. mm 1.1 KV grade cable | 1 | Set | 59 | 59 | 1 | 59
2 | Aluminium lugs for 16 sq. mm cable | 1 | each | 2 | 2 | 4 | 8
| Total A1 | [5 empty] | 67
A2 | cartage 1% of A1 | [5 empty] | 0.67
| Wastage 1% of A1 | [5 empty] | 0.67
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 0.67
| TOTAl A2 | [5 empty] | 2.01
A3 | Labour charges
| Cable jointer | 1 | Day | 617 | 617 | 0.1 | 61.7
| Khallasi | 1 | Day | 466 | 466 | 0.1 | 46.6
| Total A3 | [5 empty] | 108.3
| (A1+A2+A3) | [5 empty] | 177.31
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 4.4328
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 22.1638
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 203.9065
[6 empty] | ORSAY | 204
Computer point using 4 nos of 6 Amp 3 Pin plug socket with 16 Amp Modular switch ( on separate board ).
A1 | A1 materials
1 | Modular PVC box for 2 module. | 1 | Nos | 18 | 18 | 1 | 18
2 | Modular PVC box for 8 module. | 1 | Nos | 52.5 | 52.5 | 1 | 52.5
3 | Modular base & cover plate for 2 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
4 | Modular base & cover plate for 8 module | 1 | Nos | 91.35 | 91.35 | 1 | 91.35
5 | Single Pole 16 amps one way modular switch ISI marked | 1 | Nos | 104.4 | 104.4 | 1 | 104.4
6 | 6 pin 15/16 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 4 | 312
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 8 | 2.4
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 623.1
A2 | Cartage 1% of A1 | [5 empty] | 6.231
| Wastage 1% of A1 | [5 empty] | 6.231
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 6.231
| TOTAl A2 | [5 empty] | 18.693
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 342.25
| (A1+A2+A3) | [5 empty] | 984.043
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 24.6011
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 123.0054
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1131.6494
[6 empty] | ORSAY | 1132
Computer point using 4 nos of 6 Amp 3 Pin plug socket with 16 Amp Modular switch ( on separate board ).
A1 | A1 materials
1 | Modular GI box for 12 module. | 1 | Nos | 80.5 | 80.5 | 1 | 80.5
2 | Modular base & cover plate for 12 module | 1 | Nos | 129.15 | 129.15 | 1 | 129.15
3 | Single Pole 16 amps one way modular switch ISI marked | 1 | Nos | 104.4 | 104.4 | 2 | 208.8
4 | 6 pin 15/16 amps modular socket outlet, ISI marked | 1 | Nos | 78 | 78 | 5 | 390
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 814.65
A2 | Cartage 1% of A1 | [5 empty] | 8.1465
| Wastage 1% of A1 | [5 empty] | 8.1465
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 8.1465
| TOTAl A2 | [5 empty] | 24.4395
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.25 | 154.25
| Masson Grade II | 1 | Day | 527 | 527 | 0.175 | 92.225
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 386.275
| (A1+A2+A3) | [5 empty] | 1225.3645
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 30.6341
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 153.1706
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1409.1692
[6 empty] | ORSAY | 1409
AC point using 25 Amp 3 Pin plug socket with 25 Amp DP isolator ( on separate board ).
A1 | A1 materials
1 | 4.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. =1 X 2 = 2 + 0.10 (wastage @ 5%) =2.10m | 90 | Mtr | 2226.6 | 24.74 | 2.1 | 51.954
2 | 2.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. =1 X 1 = 1 + 0.05 (wastage @ 5%) =1.05m | 90 | Mtr | 1485.6 | 16.5067 | 1.05 | 17.332
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. =0.9 X 1 = 0.9 + 0.045 (wastage @ 5%) =0.945m | 3 | Mtr | 32.4 | 10.8 | 0.945 | 10.206
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 2 | 3
6 | Modular GI box for 2 module. | 1 | Nos | 22.5 | 22.5 | 1 | 22.5
7 | Modular base & cover plate for 2 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
8 | DP Metal Enclosures | 1 | Nos | 480 | 480 | 1 | 480
9 | DP Isolators | 1 | Nos | 276.5 | 276.5 | 1 | 276.5
10 | 3 pin 25 amps modular socket outlet, ISI marked | 1 | Nos | 151.8 | 151.8 | 1 | 151.8
11 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 8 | 2.4
12 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 1064.162
A2 | Cartage 1% of A1 | [5 empty] | 10.6416
| Wastage 1% of A1 | [5 empty] | 10.6416
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 10.6416
| TOTAl A2 | [5 empty] | 31.9249
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.3 | 139.8
| Total A3 | [5 empty] | 315.9
| (A1+A2+A3) | [5 empty] | 1411.9869
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 35.2997
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 176.4984
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1623.7849
[6 empty] | ORSAY | 1624
AC point using 25 Amp 3 Pin plug socket with 25 Amp DP isolator ( on separate board ).
A1 | A1 materials
1 | 4.0 sq.mm FRLS PVC insulated single core multistrand copper conductor. =2 X 2 = 4 + 0.20 (wastage @ 5%) =4.20m | 90 | Mtr | 2226.6 | 24.74 | 4.2 | 103.908
2 | 2.5 sq.mm FRLS PVC insulated single core multistrand copper conductor. =2 X 1 = 2 + 0.10 (wastage @ 5%) =2.10m | 90 | Mtr | 1485.6 | 16.5067 | 2.1 | 34.664
3 | FRLS PVC conduits of 20mm Dia 1.5 mm thick. =1.8 X 1 = 1.8 + 0.09 (wastage @ 5%) =1.89m | 3 | Mtr | 32.4 | 10.8 | 1.89 | 20.412
4 | 20 mm PVC bends | 1 | Nos | 6.02 | 6.02 | 1 | 6.02
5 | 20 mm iron staples/ saddles/ screws | 1 | Nos | 1.5 | 1.5 | 4 | 6
6 | Modular GI box for 2 module. | 1 | Nos | 22.5 | 22.5 | 2 | 45
7 | Modular base & cover plate for 2 module | 1 | Nos | 37.45 | 37.45 | 2 | 74.9
8 | 8 Way SPN DB With Metal door | 1 | Nos | 1348.2 | 1348.2 | 1 | 1348.2
9 | 25 ADP RCBO 30 mA | 1 | Nos | 2786 | 2786 | 1 | 2786
10 | Digital Time Switch 110 - 240 VAC 1 C/O Base/DIN 16 Pulse | 1 | Nos | 1516 | 1516 | 1 | 1516
11 | 3 pin 25 amps modular socket outlet, ISI marked | 1 | Nos | 151.8 | 151.8 | 2 | 303.6
12 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 12 | 3.6
13 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1.5 | 7.5
| Total A1 | [5 empty] | 6255.804
A2 | Cartage 1% of A1 | [5 empty] | 62.558
| Wastage 1% of A1 | [5 empty] | 62.558
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 62.558
| TOTAl A2 | [5 empty] | 187.6741
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.3 | 185.1
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.4 | 186.4
| Total A3 | [5 empty] | 450.55
| (A1+A2+A3) | [5 empty] | 6894.0281
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 172.3507
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 861.7535
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 7928.1323
[6 empty] | ORSAY | 7928
Main Panel Board.
A1 | A1 materials
1 | Indoor wall mounted , type distribution boards made out of 2 mm thk. CR sheet metal painted with 2 coats of enamel paint | 1 | Nos. | 9563 | 9563 | 1 | 9563
2 | 1 set of 125A TPN copper bus bar (18 X6 mm) | 1 | Nos | 492 | 492 | 1 | 492
3 | 1 set of 100A TPN copper bus bar(16 X 5 mm) | 1 | Nos | 394 | 394 | 2 | 788
4 | 1No 125A- 25KA - 4POLE -MCCB. | 1 | Nos | 5247.2 | 5247.2 | 1 | 5247.2
5 | 1No 63A- 10KA - 4POLE -MCB. | 1 | Nos | 1748.6 | 1748.6 | 1 | 1748.6
6 | 63A, 4-POLE Change over | 1 | Nos | 1857.8 | 1857.8 | 1 | 1857.8
7 | 40A, 4P MCB | 1 | Nos | 1748.6 | 1748.6 | 2 | 3497.2
8 | 32A, DP MCB | 1 | Nos | 550.2 | 550.2 | 3 | 1650.6
9 | 25A, DP MCB | 1 | Nos | 550.2 | 550.2 | 7 | 3851.4
10 | Digital Volt meter | 1 | Nos | 404.8 | 404.8 | 1 | 404.8
11 | Digital Ammeter | 1 | Nos | 436.8 | 436.8 | 1 | 436.8
12 | Termination Bar | 1 | Nos | 58.4 | 58.4 | 11 | 642.4
13 | Phase indicating Lamp | 1 | Nos | 32.8 | 32.8 | 6 | 196.8
14 | 32mm X 8mm bolts & nuts | 1 | Nos | 4.3 | 4.3 | 12 | 51.6
15 | Steel fastener 6 mm X 75 mm | 1 | Nos | 5.5 | 5.5 | 12 | 66
16 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 3 | 15
| Total A1 | [5 empty] | 30509.2
A2 | Cartage 1% of A1 | [5 empty] | 305.092
| Wastage 1% of A1 | [5 empty] | 305.092
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 305.092
| TOTAl A2 | [5 empty] | 915.276
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 2 | 1234
| Masson Grade II | 1 | Day | 527 | 527 | 0.75 | 395.25
| Khallasi | 1 | Day | 466 | 466 | 1.5 | 699
| Total A3 | [5 empty] | 2328.25
| (A1+A2+A3) | [5 empty] | 33752.726
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 843.8181
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 4219.0908
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 38815.6349
[6 empty] | ORSAY | 38816
125Amp, 415 V Wireable IC Cutout - 3nos in MS enclouser withj lock & key arrangements.
A1 | A1 materials
1 | MS enclouser withj lock & key arrangements | 1 | Nos. | 1148 | 1148 | 1 | 1148
2 | 125 Amp, 415 V Wireable IC Cutout | 1 | Nos | 649.6 | 649.6 | 3 | 1948.8
3 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
4 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 3127
A2 | Cartage 1% of A1 | [5 empty] | 31.27
| Wastage 1% of A1 | [5 empty] | 31.27
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 31.27
| TOTAl A2 | [5 empty] | 93.81
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.4 | 246.8
| Masson Grade II | 1 | Day | 527 | 527 | 0.2 | 105.4
| Khallasi | 1 | Day | 466 | 466 | 0.2 | 93.2
| Total A3 | [5 empty] | 445.4
| (A1+A2+A3) | [5 empty] | 3666.21
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 91.6552
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 458.2763
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 4216.1415
[6 empty] | ORSAY | 4216
Supply and installation of SPN, Double Door, Metal type Distribution Board
L.D.B (Light Distribution Board)
12 way SPN DB
Incoming :- 1 No. 32A DP MCB
Outgoing :- 10 No. 6-10 A SP MCB
A1 | A1 materials
1 | 12 way SPN DB With Metal door | 1 | Nos. | 1619.8 | 1619.8 | 1 | 1619.8
2 | 32A, DP MCB 'C' Series | 1 | Nos. | 550.2 | 550.2 | 1 | 550.2
3 | 10A, SP MCB 'C' Series | 1 | Nos. | 183.4 | 183.4 | 10 | 1834
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 4034.2
A2 | Cartage 1% of A1 | [5 empty] | 40.342
| Wastage 1% of A1 | [5 empty] | 40.342
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 40.342
| TOTAl A2 | [5 empty] | 121.026
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.52 | 320.84
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.64 | 298.24
| Total A3 | [5 empty] | 698.13
| (A1+A2+A3) | [5 empty] | 4853.356
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 121.3339
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 606.6695
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5581.3594
[6 empty] | ORSAY | 5581
Supply and installation of SPN, Double Door, Metal type Distribution Board
R.D.B (Raw power Distribution Board)
12 way SPN DB
Incoming :- 1 No. 32A DP -10 kA - MCB
Outgoing :- 10 No. 10 A SP -10 kA -MCB
A1 | A1 materials
1 | 12 way SPN DB With Metal door | 1 | Nos. | 1619.8 | 1619.8 | 1 | 1619.8
2 | 32A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 550.2 | 550.2 | 1 | 550.2
3 | 10A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 10 | 1834
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 4034.2
A2 | Cartage 1% of A1 | [5 empty] | 40.342
| Wastage 1% of A1 | [5 empty] | 40.342
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 40.342
| TOTAl A2 | [5 empty] | 121.026
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.52 | 320.84
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.64 | 298.24
| Total A3 | [5 empty] | 698.13
| (A1+A2+A3) | [5 empty] | 4853.356
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 121.3339
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 606.6695
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5581.3594
[6 empty] | ORSAY | 5581
Supply and installation of SPN, Double Door, Metal type Distribution Board
C.D.B (Computer Distribution Board)
12 way SPN DB
Incoming :- 1 No. 32A DP-10 kA -MCB
Outgoing :- 10 No. 10 A SP-10 kA -MCB
A1 | A1 materials
1 | 12 way SPN DB With Metal door | 1 | Nos. | 1619.8 | 1619.8 | 1 | 1619.8
2 | 32A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 550.2 | 550.2 | 1 | 550.2
3 | 10A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 10 | 1834
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 4034.2
A2 | Cartage 1% of A1 | [5 empty] | 40.342
| Wastage 1% of A1 | [5 empty] | 40.342
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 40.342
| TOTAl A2 | [5 empty] | 121.026
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.52 | 320.84
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.64 | 298.24
| Total A3 | [5 empty] | 698.13
| (A1+A2+A3) | [5 empty] | 4853.356
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 121.3339
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 606.6695
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5581.3594
[6 empty] | ORSAY | 5581
Supply and installation of SPN, Double Door, Metal type Distribution Board
C.D.B (Computer Distribution Board)
12 way SPN DB
Incoming :- 1 No. 32A DP-10 kA - MCB
Outgoing :- 10 No. 10 A SP-10 kA -MCB
A1 | A1 materials
1 | 12 way SPN DB With Metal door | 1 | Nos. | 1619.8 | 1619.8 | 1 | 1619.8
2 | 32A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 550.2 | 550.2 | 1 | 550.2
3 | 10A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 10 | 1834
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 4034.2
A2 | Cartage 1% of A1 | [5 empty] | 40.342
| Wastage 1% of A1 | [5 empty] | 40.342
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 40.342
| TOTAl A2 | [5 empty] | 121.026
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.52 | 320.84
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.64 | 298.24
| Total A3 | [5 empty] | 698.13
| (A1+A2+A3) | [5 empty] | 4853.356
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 121.3339
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 606.6695
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5581.3594
[6 empty] | ORSAY | 5581
Supply and installation of SPN, Double Door, Metal type Distribution Board
C.D.B (Computer Distribution Board)
8 way SPN DB
Incoming :- 1 No. 25A DP-10 kA - MCB
Out going :- 6 No. 10 A SP -10 kA -MCB
A1 | A1 materials
1 | 8 way SPN DB With Metal door | 1 | Nos. | 1348.2 | 1348.2 | 1 | 1348.2
2 | 25A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 550.2 | 550.2 | 1 | 550.2
3 | 10A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 6 | 1100.4
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 3029
A2 | Cartage 1% of A1 | [5 empty] | 30.29
| Wastage 1% of A1 | [5 empty] | 30.29
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 30.29
| TOTAl A2 | [5 empty] | 90.87
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.52 | 320.84
| Masson Grade II | 1 | Day | 527 | 527 | 0.15 | 79.05
| Khallasi | 1 | Day | 466 | 466 | 0.64 | 298.24
| Total A3 | [5 empty] | 698.13
| (A1+A2+A3) | [5 empty] | 3818
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 95.45
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 477.25
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 4390.7
[6 empty] | ORSAY | 4391
Supply and installation of SPN, Double Door, Metal type Distribution Board
U.P.S Incoming DB
4 way SPN DB
40 Amp DP-10 kA - MCB – 2 nos (1main & 1 spare).
A1 | A1 materials
1 | 4 way SPN DB With Metal door | 1 | Nos. | 1086.4 | 1086.4 | 1 | 1086.4
2 | 40A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 884.8 | 884.8 | 2 | 1769.6
3 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
4 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 2886.2
A2 | Cartage 1% of A1 | [5 empty] | 28.862
| Wastage 1% of A1 | [5 empty] | 28.862
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 28.862
| TOTAl A2 | [5 empty] | 86.586
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.38 | 234.46
| Masson Grade II | 1 | Day | 527 | 527 | 0.12 | 63.24
| Khallasi | 1 | Day | 466 | 466 | 0.4 | 186.4
| Total A3 | [5 empty] | 484.1
| (A1+A2+A3) | [5 empty] | 3456.886
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 86.4222
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 432.1107
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 3975.4189
[6 empty] | ORSAY | 3975
Supply and installation of SPN, Double Door, Metal type Distribution Board
U.P.S Outgoing DB
4 way SPN DB
Incoming :- 40 Amp DP-10 kA - MCB – 1 No
Out going :- 2 No. 25 A SP-10 kA - MCB
A1 | A1 materials
1 | 4 way SPN DB With Metal door | 1 | Nos. | 1086.4 | 1086.4 | 1 | 1086.4
2 | 40A, DP MCB 'C' Series -10 kA - | 1 | Nos. | 884.8 | 884.8 | 1 | 884.8
3 | 25A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 2 | 366.8
4 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
5 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
6 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 2368.2
A2 | Cartage 1% of A1 | [5 empty] | 23.682
| Wastage 1% of A1 | [5 empty] | 23.682
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 23.682
| TOTAl A2 | [5 empty] | 71.046
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.38 | 234.46
| Masson Grade II | 1 | Day | 527 | 527 | 0.12 | 63.24
| Khallasi | 1 | Day | 466 | 466 | 0.4 | 186.4
| Total A3 | [5 empty] | 484.1
| (A1+A2+A3) | [5 empty] | 2923.346
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 73.0837
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 365.4183
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 3361.8479
[6 empty] | ORSAY | 3362
Supply and installation of VTPN, Double Door, Metal type Distribution Board
U.P.S Outgoing DB
6 way VTPN DB
Incoming :- 1 No. 63A 4P MCB, 63A -415V-4P Isolator.
Out going :- 5 No. 20A TP -10 kA - MCB
3 No. 25A SP -10 kA - MCB
A1 | A1 materials
1 | 6 way VTPN DB With Metal door | 1 | Nos. | 7204.4 | 7204.4 | 1 | 7204.4
2 | 63A, 4P MCB 'C' Series -10 kA - | 1 | Nos. | 1748.6 | 1748.6 | 1 | 1748.6
3 | 63A, 4P Isolator - 415V | 1 | Nos. | 801.5 | 801.5 | 1 | 801.5
4 | 20A, TP MCB 'C' Series -10 kA - | 1 | Nos. | 897.4 | 897.4 | 5 | 4487
5 | 25A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 3 | 550.2
6 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
7 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
8 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 14821.9
A2 | Cartage 1% of A1 | [5 empty] | 148.219
| Wastage 1% of A1 | [5 empty] | 148.219
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 148.219
| TOTAl A2 | [5 empty] | 444.657
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.64 | 394.88
| Masson Grade II | 1 | Day | 527 | 527 | 0.2 | 105.4
| Khallasi | 1 | Day | 466 | 466 | 0.75 | 349.5
| Total A3 | [5 empty] | 849.78
| (A1+A2+A3) | [5 empty] | 16116.337
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 402.9084
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2014.5421
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 18533.7876
[6 empty] | ORSAY | 18534
Supply and installation of VTPN, Double Door, Metal type Distribution Board
U.P.S Outgoing DB
4 way VTPN DB
Incoming :-1 No. 125A MCCB-16kA -415V-4P Isolator.
Out going :- 12 No. 32A SP -10 kA - MCB
A1 | A1 materials
1 | 4 way VTPN DB With Metal door | 1 | Nos. | 6549.2 | 6549.2 | 1 | 6549.2
2 | 125A MCCB-16kA | 1 | Nos. | 5247.2 | 5247.2 | 1 | 5247.2
3 | 125A, 4P Isolator - 415V | 1 | Nos. | 1088.5 | 1088.5 | 1 | 1088.5
4 | 32A, SP MCB 'C' Series -10 kA - | 1 | Nos. | 183.4 | 183.4 | 12 | 2200.8
5 | 6 mm dia Rag Bolts with Nuts | 1 | Nos | 6 | 6 | 4 | 24
6 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
7 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 1 | 5
| Total A1 | [5 empty] | 15115.9
A2 | Cartage 1% of A1 | [5 empty] | 151.159
| Wastage 1% of A1 | [5 empty] | 151.159
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 151.159
| TOTAl A2 | [5 empty] | 453.477
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.64 | 394.88
| Masson Grade II | 1 | Day | 527 | 527 | 0.2 | 105.4
| Khallasi | 1 | Day | 466 | 466 | 0.75 | 349.5
| Total A3 | [5 empty] | 849.78
| (A1+A2+A3) | [5 empty] | 16419.157
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 410.4789
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 2052.3946
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 18882.0305
[6 empty] | ORSAY | 18882
Recess LED lights fittings (36W).
A1 | A1 materials
1 | 36W LED Recessed 2X2 | 1 | Nos. | 2800 | 2800 | 1 | 2800
| Total A1 | [5 empty] | 2800
A2 | Cartage 1% of A1 | [5 empty] | 28
| Wastage 1% of A1 | [5 empty] | 28
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 28
| TOTAl A2 | [5 empty] | 84
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.3 | 185.1
| Khallasi | 1 | Day | 466 | 466 | 0.2 | 93.2
| Total A3 | [5 empty] | 278.3
| (A1+A2+A3) | [5 empty] | 3162.3
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 79.0575
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 395.2875
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 3636.645
[6 empty] | ORSAY | 3637
Recess LED lights fittings (18W).
A1 | A1 materials
1 | 18W squre LED Downlighter | 1 | Nos. | 1085 | 1085 | 1 | 1085
| Total A1 | [5 empty] | 1085
A2 | Cartage 1% of A1 | [5 empty] | 10.85
| Wastage 1% of A1 | [5 empty] | 10.85
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 10.85
| TOTAl A2 | [5 empty] | 32.55
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.3 | 185.1
| Khallasi | 1 | Day | 466 | 466 | 0.2 | 93.2
| Total A3 | [5 empty] | 278.3
| (A1+A2+A3) | [5 empty] | 1395.85
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 34.8963
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 174.4812
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1605.2275
[6 empty] | ORSAY | 1605
Recess LED lights fittings ( 6W) of spot.
A1 | A1 materials
1 | 6W Recess LED spot lights | 1 | Nos. | 385 | 385 | 1 | 385
| Total A1 | [5 empty] | 385
A2 | Cartage 1% of A1 | [5 empty] | 3.85
| Wastage 1% of A1 | [5 empty] | 3.85
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.85
| TOTAl A2 | [5 empty] | 11.55
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 193.3
| (A1+A2+A3) | [5 empty] | 589.85
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 14.7462
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 73.7313
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 678.3275
[6 empty] | ORSAY | 678
Recess LED lights fittings ( 12W) of spot.
A1 | A1 materials
1 | 12W Recess LED spot lights | 1 | Nos. | 595 | 595 | 1 | 595
| Total A1 | [5 empty] | 595
A2 | Cartage 1% of A1 | [5 empty] | 5.95
| Wastage 1% of A1 | [5 empty] | 5.95
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 5.95
| TOTAl A2 | [5 empty] | 17.85
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 193.3
| (A1+A2+A3) | [5 empty] | 806.15
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 20.1537
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 100.7687
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 927.0725
[6 empty] | ORSAY | 927
Surface LED lights fittings ( 12W) .
A1 | A1 materials
1 | 12W Round/Squre Surface mounted LED | 1 | Nos. | 700 | 700 | 1 | 700
| Total A1 | [5 empty] | 700
A2 | Cartage 1% of A1 | [5 empty] | 7
| Wastage 1% of A1 | [5 empty] | 7
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 7
| TOTAl A2 | [5 empty] | 21
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 246
| (A1+A2+A3) | [5 empty] | 967
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 24.175
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 120.875
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1112.05
[6 empty] | ORSAY | 1112
400 mm sweep High Flo Wall fan.
A1 | A1 materials
1 | 400 mm sweep High Flo Wall fan | 1 | Nos. | 1625 | 1625 | 1 | 1625
| Total A1 | [5 empty] | 1625
A2 | Cartage 1% of A1 | [5 empty] | 16.25
| Wastage 1% of A1 | [5 empty] | 16.25
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 16.25
| TOTAl A2 | [5 empty] | 48.75
A3 | Labour charges
| Wireman Grade I | 1 | Day | 679 | 679 | 0.2 | 135.8
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 617 | 617 | 0.15 | 92.55
| Total A3 | [5 empty] | 281.05
| (A1+A2+A3) | [5 empty] | 1954.8
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 48.87
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 244.35
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 2248.02
[6 empty] | ORSAY | 2248
400 mm sweep cabin fan.
A1 | A1 materials
1 | 400 mm sweep cabin fan | 1 | Nos. | 1679.6 | 1679.6 | 1 | 1679.6
| Total A1 | [5 empty] | 1679.6
A2 | Cartage 1% of A1 | [5 empty] | 16.796
| Wastage 1% of A1 | [5 empty] | 16.796
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 16.796
| TOTAl A2 | [5 empty] | 50.388
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 246
| (A1+A2+A3) | [5 empty] | 1975.988
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 49.3997
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 246.9985
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 2272.3862
[6 empty] | ORSAY | 2272
150 mm sweep heavy duty Exhust fan.
A1 | A1 materials
1 | 150 mm sweep heavy duty Exhust fan | 1 | Nos. | 1202.5 | 1202.5 | 1 | 1202.5
| Total A1 | [5 empty] | 1202.5
A2 | Cartage 1% of A1 | [5 empty] | 12.025
| Wastage 1% of A1 | [5 empty] | 12.025
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 12.025
| TOTAl A2 | [5 empty] | 36.075
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 246
| (A1+A2+A3) | [5 empty] | 1484.575
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 37.1144
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 185.5719
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1707.2613
[6 empty] | ORSAY | 1707
225 mm sweep heavy duty Exhust fan.
A1 | A1 materials
1 | 225 mm sweep heavy duty Exhust fan | 1 | Nos. | 1277.25 | 1277.25 | 1 | 1277.25
| Total A1 | [5 empty] | 1277.25
A2 | Cartage 1% of A1 | [5 empty] | 12.7725
| Wastage 1% of A1 | [5 empty] | 12.7725
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 12.7725
| TOTAl A2 | [5 empty] | 38.3175
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 246
| (A1+A2+A3) | [5 empty] | 1561.5675
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 39.0392
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 195.1959
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1795.8026
[6 empty] | ORSAY | 1796
300 mm sweep heavy duty Exhust fan.
A1 | A1 materials
1 | 300 mm sweep heavy duty Exhust fan | 1 | Nos. | 1397.5 | 1397.5 | 1 | 1397.5
| Total A1 | [5 empty] | 1397.5
A2 | Cartage 1% of A1 | [5 empty] | 13.975
| Wastage 1% of A1 | [5 empty] | 13.975
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 13.975
| TOTAl A2 | [5 empty] | 41.925
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 246
| (A1+A2+A3) | [5 empty] | 1685.425
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 42.1356
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 210.6781
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1938.2387
[6 empty] | ORSAY | 1938
1200 mm sweep celing fan.
A1 | A1 materials
1 | 1200 mm sweep celing fan | 1 | Nos. | 1309.75 | 1309.75 | 1 | 1309.75
| Total A1 | [5 empty] | 1309.75
A2 | Cartage 1% of A1 | [5 empty] | 13.0975
| Wastage 1% of A1 | [5 empty] | 13.0975
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 13.0975
| TOTAl A2 | [5 empty] | 39.2925
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.2 | 123.4
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 193.3
| (A1+A2+A3) | [5 empty] | 1542.3425
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 38.5586
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 192.7928
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1773.6939
[6 empty] | ORSAY | 1774
Modular type step fan regulator.
A1 | A1 materials
1 | Step type Fan Regulator | 1 | Nos. | 118.8 | 118.8 | 1 | 118.8
2 | Modular GI box for 2module 18 swg | 1 | Nos | 22.5 | 22.5 | 1 | 22.5
3 | Modular base & cover plate for 1 module | 1 | Nos | 37.45 | 37.45 | 1 | 37.45
4 | PVC fastener 40mm long | 1 | Nos | 0.3 | 0.3 | 4 | 1.2
5 | Cement, paint, sand etc. | 1 | LS/Mtr | 5 | 5 | 0.2 | 1
| Total A1 | [5 empty] | 180.95
A2 | Cartage 1% of A1 | [5 empty] | 1.8095
| Wastage 1% of A1 | [5 empty] | 1.8095
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 1.8095
| TOTAl A2 | [5 empty] | 5.4285
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.05 | 30.85
| Masson Grade II | 1 | Day | 527 | 527 | 0.005 | 2.635
| Khallasi | 1 | Day | 466 | 466 | 0.075 | 34.95
| Total A3 | [5 empty] | 68.435
| (A1+A2+A3) | [5 empty] | 254.8135
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 6.3703
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 31.8517
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 293.0355
[6 empty] | ORSAY | 293
fan-hook,by cutting roof slab and welding 10 mm dia..
A1 | A1 materials
1 | fan-hook,10 mm dia. | 1 | Nos. | 70 | 70 | 1 | 70
| Total A1 | [5 empty] | 70
A2 | Cartage 1% of A1 | [5 empty] | 0.7
| Wastage 1% of A1 | [5 empty] | 0.7
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 0.7
| TOTAl A2 | [5 empty] | 2.1
A3 | Labour charges
| Masson Grade II | 1 | Day | 527 | 527 | 0.075 | 39.525
| Khallasi | 1 | Day | 466 | 466 | 0.04 | 18.64
| Total A3 | [5 empty] | 58.165
| (A1+A2+A3) | [5 empty] | 130.265
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 3.2566
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 16.2831
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 149.8048
[6 empty] | ORSAY | 150
20W LED Batten lights fittings
A1 | A1 materials
1 | 20W LED Batten lights fittings | 1 | Nos. | 595 | 595 | 1 | 595
| Total A1 | [5 empty] | 595
A2 | Cartage 1% of A1 | [5 empty] | 5.95
| Wastage 1% of A1 | [5 empty] | 5.95
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 5.95
| TOTAl A2 | [5 empty] | 17.85
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.25 | 154.25
| Khallasi | 1 | Day | 466 | 466 | 0.15 | 69.9
| Total A3 | [5 empty] | 224.15
| (A1+A2+A3) | [5 empty] | 837
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 20.925
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 104.625
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 962.55
[6 empty] | ORSAY | 963
Batten LED lights fittings (2x20W)
A1 | A1 materials
1 | 20 W LED Batten light | 1 | Nos. | 605.5 | 605.5 | 2 | 1211
2 | Twin LED Batten Frame | 1 | Nos. | 290.5 | 290.5 | 1 | 290.5
3 | fan-hook,10 mm dia. | 1 | Nos. | 70 | 70 | 2 | 140
4 | Down Rod 600mm long | 1 | Nos. | 150 | 150 | 2 | 300
| Total A1 | [5 empty] | 1941.5
A2 | Cartage 1% of A1 | [5 empty] | 19.415
| Wastage 1% of A1 | [5 empty] | 19.415
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 19.415
| TOTAl A2 | [5 empty] | 58.245
A3 | Labour charges
| Wireman Grade I | 1 | Day | 679 | 679 | 0.3 | 203.7
| Masson Grade II | 1 | Day | 527 | 527 | 0.1 | 52.7
| Khallasi | 1 | Day | 617 | 617 | 0.2 | 123.4
| Total A3 | [5 empty] | 379.8
| (A1+A2+A3) | [5 empty] | 2379.545
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 59.4886
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 297.4431
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 2736.4767
[6 empty] | ORSAY | 2736
9W LED Bulb fittings with angle holder
A1 | A1 materials
1 | 9W LED Bulb | 1 | Nos. | 251.3 | 251.3 | 1 | 251.3
| Total A1 | [5 empty] | 251.3
A2 | Cartage 1% of A1 | [5 empty] | 2.513
| Wastage 1% of A1 | [5 empty] | 2.513
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 2.513
| TOTAl A2 | [5 empty] | 7.539
A3 | Labour charges
| Wireman Grade I | 1 | Day | 679 | 679 | 0.175 | 118.825
| Khallasi | 1 | Day | 617 | 617 | 0.075 | 46.275
| Total A3 | [5 empty] | 165.1
| (A1+A2+A3) | [5 empty] | 423.939
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 10.5985
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 52.9924
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 487.5299
[6 empty] | ORSAY | 488
Call bell Remote Controlled with Battery.
A1 | A1 materials
1 | Call bell Remote Controlled with Battery | 1 | Nos. | 350 | 350 | 1 | 350
| Total A1 | [5 empty] | 350
A2 | Cartage 1% of A1 | [5 empty] | 3.5
| Wastage 1% of A1 | [5 empty] | 3.5
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.5
| TOTAl A2 | [5 empty] | 10.5
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.05 | 30.85
| Khallasi | 1 | Day | 466 | 466 | 0.005 | 2.33
| Total A3 | [5 empty] | 33.18
| (A1+A2+A3) | [5 empty] | 393.68
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 9.842
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 49.21
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 452.732
[6 empty] | ORSAY | 453
Earthing with G.I. earth plate of size 600 mm X 600 mm X 6.36 mm thick including accessories with charcoal / coke and salt as required.
A1 | A1 materials
1 | 600 mm X 600 mm X 6.36 mm thick G.I. plate | 1 | Nos. | 1438 | 1438 | 1 | 1438
2 | 20 mm dia. G.I. pipe (medium class) = 2.70 + 0.14 (Wastage @ 5%) = 2.84m | 1 | Mtr. | 111 | 111 | 2.84 | 315.24
3 | CI/MS cover plate hinged to frame with Locking arrangement | 1 | Nos. | 277 | 277 | 1 | 277
4 | Funnel | 1 | Nos. | 19 | 19 | 1 | 19
5 | G.I. nuts and through bolts with washer | 1 | Nos. | 26 | 26 | 1 | 26
6 | Charcoal | 1 | Kg. | 8 | 8 | 96 | 768
7 | Salt | 1 | Kg. | 8 | 8 | 5 | 40
8 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | 1 | Nos. | 4 | 4 | 50 | 200
9 | Cement | 1 | tonne | 6300 | 6300 | 0.01 | 63
10 | Fine sand | 1 | cum | 806 | 806 | 0.03 | 24.18
| Total A1 | [5 empty] | 3170.42
A2 | Cartage 1% of A1 | [5 empty] | 31.7042
| Wastage 1% of A1 | [5 empty] | 31.7042
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 31.7042
| TOTAl A2 | [5 empty] | 95.1126
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.5 | 308.5
| Khallasi | 1 | Day | 466 | 466 | 0.5 | 233
| Mason, Grade 2 | 1 | Day | 527 | 527 | 0.2 | 105.4
| Beldar/ coolie | 1 | Day | 466 | 466 | 1.45 | 675.7
| Total A3 | [5 empty] | 1322.6
| (A1+A2+A3) | [5 empty] | 4588.1326
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 114.7033
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 573.5166
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5276.3525
[6 empty] | ORSAY | 5276
Earthing with Copper earth plate of size 600 mm X 600 mm X 3.18 mm mm thick including accessories with charcoal / coke and salt as required.
A1 | A1 materials
1 | 600 mm X 600 mm X 3.18 mm thick copper plate (10.5 kg) | 1 | Nos. | 5649 | 5649 | 1 | 5649
2 | 20 mm dia. G.I. pipe (medium class) = 2.70 + 0.14 (Wastage @ 5%) = 2.84m | 1 | Mtr. | 111 | 111 | 2.84 | 315.24
3 | CI/MS cover plate hinged to frame with Locking arrangement | 1 | Nos. | 277 | 277 | 1 | 277
4 | Funnel | 1 | Nos. | 19 | 19 | 1 | 19
5 | G.I. nuts and through bolts with washer | 1 | Nos. | 26 | 26 | 1 | 26
6 | Charcoal | 1 | Kg. | 8 | 8 | 96 | 768
7 | Salt | 1 | Kg. | 8 | 8 | 5 | 40
8 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | 1 | Nos. | 4 | 4 | 50 | 200
9 | Cement | 1 | tonne | 6300 | 6300 | 0.01 | 63
10 | Fine sand | 1 | cum | 806 | 806 | 0.03 | 24.18
| Total A1 | [5 empty] | 7381.42
A2 | Cartage 1% of A1 | [5 empty] | 73.8142
| Wastage 1% of A1 | [5 empty] | 73.8142
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 73.8142
| TOTAl A2 | [5 empty] | 221.4426
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.5 | 308.5
| Khallasi | 1 | Day | 466 | 466 | 0.5 | 233
| Mason, Grade 2 | 1 | Day | 527 | 527 | 0.2 | 105.4
| Beldar/ coolie | 1 | Day | 466 | 466 | 1.45 | 675.7
| Total A3 | [5 empty] | 1322.6
| (A1+A2+A3) | [5 empty] | 8925.4626
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 223.1366
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 1115.6828
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 10264.282
[6 empty] | ORSAY | 10264
25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe
COST FOR 10 METERS
A1 | A1 materials
1 | 25 mm X 5 mm G.I. strip (1.0 kg/mtr) = 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg | 1 | Kg. | 57 | 57 | 10.5 | 598.5
2 | 40 mm dia. G.I. pipe (medium class) = 10.0 + 0.5 (Wastage @ 5%) = 10.5m | 1 | Mtr. | 239 | 239 | 10.5 | 2509.5
3 | 40 mm dia. G.I. bend (medium class) | 1 | Nos. | 57 | 57 | 1 | 57 | `
| Total A1 | [5 empty] | 3165
A2 | Cartage 1% of A1 | [5 empty] | 31.65
| Wastage 1% of A1 | [5 empty] | 31.65
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 31.65
| TOTAl A2 | [5 empty] | 94.95
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.25 | 154.25
| Khallasi | 1 | Day | 466 | 466 | 0.25 | 116.5
| Beldar/ coolie | 1 | Day | 466 | 466 | 0.33 | 153.78
| Total A3 | [5 empty] | 424.53
| (A1+A2+A3) | [5 empty] | 3684.48
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 92.112
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 460.56
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 4237.152
A7 | Rate / Mtr=A6/10 | [5 empty] | 423.7152
[6 empty] | ORSAY | 424
25 mm X 5 mm G.I. strip on surface or in recess.
COST FOR 10 METERS
A1 | A1 materials
1 | 25 mm X 5 mm G.I. strip (1.0 kg/mtr) = 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg | 1 | Kg. | 57 | 57 | 10.5 | 598.5
2 | GI saddle 20mm x 3mm | 1 | Nos. | 2.5 | 2.5 | 17 | 42.5
3 | Al. Alloy/ cadmium plated iron screws, 20 mm | 1 | Nos. | 0.5 | 0.5 | 34 | 17
4 | PVC fastener 40mm long | 1 | Nos. | 0.3 | 0.3 | 17 | 5.1
| Total A1 | [5 empty] | 663.1
A2 | Cartage 1% of A1 | [5 empty] | 6.631
| Wastage 1% of A1 | [5 empty] | 6.631
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 6.631
| TOTAl A2 | [5 empty] | 19.893
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.5 | 308.5
| Mason, Grade 2 | 1 | Day | 527 | 527 | 0.25 | 131.75
| Khallasi | 1 | Day | 466 | 466 | 0.75 | 349.5
| Total A3 | [5 empty] | 789.75
| (A1+A2+A3) | [5 empty] | 1472.743
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 36.8186
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 184.0929
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 1693.6544
A7 | Rate / Mtr=A6/10 | [5 empty] | 169.3654
[6 empty] | ORSAY | 169
4.00 mm dia copper wire in 15 mm dia G.I. pipe
COST FOR 10 METERS
A1 | A1 materials
1 | 15 mm dia. G.I. pipe (medium class) = 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg | 1 | Mtr. | 88 | 88 | 10.5 | 924
2 | 8 SWG copper wire (4.0 mm dia) = ( 0.117 kg/mtr) = 10x0.117 = 1.17 kg | 1 | Kg. | 540 | 540 | 1.17 | 631.8
| Total A1 | [5 empty] | 1555.8
A2 | Cartage 1% of A1 | [5 empty] | 15.558
| Wastage 1% of A1 | [5 empty] | 15.558
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 15.558
| TOTAl A2 | [5 empty] | 46.674
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.17 | 104.89
| Khallasi | 1 | Day | 466 | 466 | 0.17 | 79.22
| Beldar/ coolie | 1 | Day | 466 | 466 | 0.33 | 153.78
| Total A3 | [5 empty] | 337.89
| (A1+A2+A3) | [5 empty] | 1940.364
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 48.5091
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 242.5455
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 2231.4186
A7 | Rate / Mtr=A6/10 | [5 empty] | 223.1419
[6 empty] | ORSAY | 223
4.00 mm dia copper wire in 15 mm dia G.I. pipe
COST FOR 50 METERS
A1 | A1 materials
1 | 8 SWG copper wire (4.0 mm dia) ( 0.117 kg/mtr) = 50x0.117 = 5.85 kg | 1 | Kg. | 540 | 540 | 5.85 | 3159
2 | G.I. Hooks made of 8 SWG GI wire/ GI clip | 1 | Nos. | 2 | 2 | 85 | 170
3 | PVC fastener 40mm long | 1 | Nos. | 0.3 | 0.3 | 85 | 25.5
| Total A1 | [5 empty] | 3354.5
A2 | Cartage 1% of A1 | [5 empty] | 33.545
| Wastage 1% of A1 | [5 empty] | 33.545
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 33.545
| TOTAl A2 | [5 empty] | 100.635
A3 | Labour charges
| Wireman Grade I | 1 | Day | 617 | 617 | 0.75 | 462.75
| Mason, Grade 2 | 1 | Day | 527 | 527 | 0.5 | 263.5
| Khallasi | 1 | Day | 466 | 466 | 1.25 | 582.5
| Total A3 | [5 empty] | 1308.75
| (A1+A2+A3) | [5 empty] | 4763.885
A4 | Overhead charges 2.5% on(A1+A2+A3) | [5 empty] | 119.0971
A5 | Contractors profit 12.5% on(A1+A2+A3) | [5 empty] | 595.4856
A6 | Total(A1+A2+A3+A4+A5) | [5 empty] | 5478.4677
A7 | Rate / Mtr=A6/50 | [5 empty] | 109.5694
[6 empty] | ORSAY | 110
A1 | A1 materials
1 | Telephone socket outlet modular type | 1 | Mtr | 95 | 95 | 1 | 95
| Al alloy/ cadmium iron screws 25mm | 100 | Nos | 50 | 0.5 | 2 | 1
| Total A1 | [5 empty] | 96
A2 | cartage 1% of A1 | [5 empty] | 0.96
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 0.96
| TOTAl A2 | [5 empty] | 1.92
A3 | Labour charges
| wireman grade 1 | 1 | Day | 273.5 | 273.5 | 0.05 | 13.675
| Helper | 1 | Day | 213.5 | 213.5 | 0.05 | 10.675
| Total A3 | [5 empty] | 24.35
| (A1+A2+A3) | [5 empty] | 122.27
A4 | Overhead charges 10% on(A1+A2+A3) | [5 empty] | 12.227
A5 | Total(A1+A2+A3+A4) | [5 empty] | 134.497
A6 | Cess1% OF A5 | [5 empty] | 1.345
| (A5 + A6) | [5 empty] | 135.842
[6 empty] | orsay | 136
Supplying and fixing of Call Bell / Buzzer ISI marked suitable for DC /AC single phase 230 volts complete as required.
A1 | A1 materials
1 | Call bell/ buzzer single phase DC/AC ISI marked | 1 | Nos | 82 | 82 | 1 | 82
| Al alloy/ cadmium iron screws 25mm | 100 | Nos | 50 | 0.5 | 2 | 1
| Total A1 | [5 empty] | 83
A2 | cartage 1% of A1 | [5 empty] | 0.83
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 0.83
| TOTAl A2 | [5 empty] | 1.66
A3 | Labour charges
| wireman grade 1 | 1 | Day | 273.5 | 273.5 | 0.05 | 13.675
| Helper | 1 | Day | 213.5 | 213.5 | 0.05 | 10.675
| Total A3 | [5 empty] | 24.35
| (A1+A2+A3) | [5 empty] | 109.01
A4 | Overhead charges 10% on(A1+A2+A3) | [5 empty] | 10.901
A5 | Total(A1+A2+A3+A4) | [5 empty] | 119.911
A6 | Cess1% OF A5 | [5 empty] | 1.1991
| (A5 + A6) | [5 empty] | 121.1101
[6 empty] | orsay | 121.1
Supply , fixing of all required cat – 6 LAN wiring in PVC pipe (keeping precaution to keep wiring at least 1’ from electrical wiring) as per direction of EIC .
A | Resessed wiring to Telephone point with 2 pair telephone cable
Cost for 50 Mtr
A1 | A1 materials
1 | cat – 6 LAN insulated unarmoured, data cable | 1 | Mtr | 7.5 | 7.5 | 50.5 | 378.75
| Total A1 | [5 empty] | 378.75
A2 | cartage 1% of A1 | [5 empty] | 3.7875
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.7875
| wastage 1% of A | [5 empty] | 3.7875
| TOTAl A2 | [5 empty] | 11.3625
A3 | Labour charges
| wireman grade 1 | 1 | Day | 273.5 | 273.5 | 2 | 547
| Helper | 1 | Day | 213.5 | 213.5 | 2 | 427
| Total A3 | [5 empty] | 974
| (A1+A2+A3) | [5 empty] | 1364.1125
A4 | Overhead charges 10% on(A1+A2+A3) | [5 empty] | 136.4112
A5 | Total(A1+A2+A3+A4) | [5 empty] | 1500.5238
A6 | Cess1% OF A5 | [5 empty] | 15.0052
| (A5 + A6) | [5 empty] | 1515.529
A7 | Rare/mtr=(A5+A6/50) | [5 empty] | 30.3106
[6 empty] | orsay | 30.3
Supply , fixing of all required with RJ 45 connector with cat – 6-LANand cat-5 cable with termination & 2Mt. Patch code with complete in all respect including IO box of ( D Link / Amps ) as per direction of EIC .make : D link wire / box.
A1 | A1 materials
1 | RJ 45 connecto socket outlet modular type | 1 | nos | 350 | 350 | 1 | 350
| Al alloy/ cadmium iron screws 25mm | 100 | Nos | 50 | 0.5 | 2 | 1
| Total A1 | [5 empty] | 351
A2 | cartage 1% of A1 | [5 empty] | 3.51
| Hire chargesfor T&P 1% OF A1 | [5 empty] | 3.51
| TOTAl A2 | [5 empty] | 7.02
A3 | Labour charges
| wireman grade 1 | 1 | Day | 273.5 | 273.5 | 0.05 | 13.675
| Helper | 1 | Day | 213.5 | 213.5 | 0.05 | 10.675
| Total A3 | [5 empty] | 24.35
| (A1+A2+A3) | [5 empty] | 382.37
A4 | Overhead charges 10% on(A1+A2+A3) | [5 empty] | 38.237
A5 | Total(A1+A2+A3+A4) | [5 empty] | 420.607
A6 | Cess1% OF A5 | [5 empty] | 4.2061
| (A5 + A6) | [5 empty] | 424.8131
[6 empty] | orsay | 424.8

## Basic Rate of Material (hidden)
BASIC RATE OF MATERIAL
Note:- These rates are exclusive of contractor’s profit, overheads and carriage and any taxes etc.
S.l No | Description | Unit | M.R.P. | Market Discount (%) | Market Rate
Wires (FRLS PVC insulated single core multistrand copper conductor.)
1 | 1.0 sq.mm | coil | 1039 | 40 | 623.4
2 | 1.5 sq.mm | coil | 1547 | 40 | 928.2
3 | 2.5 sq.mm | coil | 2476 | 40 | 1485.6
4 | 4.0 sq.mm | coil | 3711 | 40 | 2226.6
5 | 6.0 sq.mm | coil | 5526 | 40 | 3315.6
6 | 10.0 sq.mm | coil | 9730 | 40 | 5838
7 | 16.0 sq.mm | coil | 15626 | 40 | 9375.6
Cable (4 Core, XLPE Insulated, Aluminum Armoured Cable )
8 | 4.0 sq.mm | Mtr | 99 | 30 | 69.3
9 | 6.0 sq.mm | Mtr | 113 | 30 | 79.1
10 | 10.0 sq.mm | Mtr | 141 | 30 | 98.7
11 | 16.0 sq.mm | Mtr | 161 | 30 | 112.7
12 | 25.0 sq.mm | Mtr | 220 | 30 | 154
13 | 35.0 sq.mm | Mtr | 269 | 30 | 188.3
14 | 50.0 sq.mm | Mtr | 347 | 30 | 242.9
15 | 70.0 sq.mm | Mtr | 470 | 30 | 329
16 | 95.0 sq.mm | Mtr | 573 | 30 | 401.1
Cable ( 3½ Core, XLPE Insulated, Aluminum Armoured Cable )
17 | 25.0 sq.mm | Mtr | 203 | 30 | 142.1
18 | 35.0 sq.mm | Mtr | 242 | 30 | 169.4
19 | 50.0 sq.mm | Mtr | 314 | 30 | 219.8
20 | 70.0 sq.mm | Mtr | 427 | 30 | 298.9
21 | 95.0 sq.mm | Mtr | 515 | 30 | 360.5
22 | 120.0 sq.mm | Mtr | 644 | 30 | 450.8
23 | 150.0 sq.mm | Mtr | 762 | 30 | 533.4
24 | 185.0 sq.mm | Mtr | 951 | 30 | 665.7
25 | 240.0 sq.mm | Mtr | 1197 | 30 | 837.9
26 | 300.0 sq.mm | Mtr | 1467 | 30 | 1026.9
27 | 400.0 sq.mm | Mtr | 1868 | 30 | 1307.6
28 | 500.0 sq.mm | Mtr | 2539 | 30 | 1777.3
29 | 630.0 sq.mm | Mtr | 3450 | 30 | 2415
Cable ( 4 Core, XLPE Insulated, Copper Armoured Cable )
30 | 4.0 sq.mm | Mtr | 201 | 30 | 140.7
31 | 6.0 sq.mm | Mtr | 290 | 30 | 203
32 | 10.0 sq.mm | Mtr | 480 | 30 | 336
33 | 16.0 sq.mm | Mtr | 715 | 30 | 500.5
FRLS PVC Conduit Pipes High Mechanical Stress 1.5 mm thick.
34 | 16 mm Dia | each | 27.4 | 10 | 24.66
35 | 20 mm Dia | each | 36 | 10 | 32.4
36 | 25 mm Dia | each | 47 | 10 | 42.3
37 | 32 mm Dia | each | 75 | 10 | 67.5
38 | 40 mm Dia | each | 107 | 10 | 96.3
39 | 50 mm Dia | each | 160 | 10 | 144
PVCBands
40 | 16 mm Dia | each | 8.6 | 30 | 6.02
41 | 20 mm Dia | each | 8.6 | 30 | 6.02
42 | 25 mm Dia | each | 13.9 | 30 | 9.73
43 | 32 mm Dia | each | 38.1 | 30 | 26.67
44 | 40 mm Dia | each | 76 | 30 | 53.2
45 | 50 mm Dia | each | 108 | 30 | 75.6
PVCBCouplers
46 | 20 mm Dia | each | 7.6 | 30 | 5.32
47 | 25 mm Dia | each | 12.4 | 30 | 8.68
48 | 32 mm Dia | each | 18.1 | 30 | 12.67
49 | 40 mm Dia | each | 24.8 | 30 | 17.36
50 | 50 mm Dia | each | 32.4 | 30 | 22.68
Iron staples/ saddles/ screws
51 | 20 mm | each | 1.5 | 0 | 1.5
52 | 25 mm | each | 2.1 | 0 | 2.1
53 | 32 mm | each | 3.15 | 0 | 3.15
54 | 40 mm | each | 4.1 | 0 | 4.1
55 | 50 mm | each | 5.4 | 0 | 5.4
Junction box
56 | 20 mm PVC junction box, one way | each | 10 | 0 | 10
Metal Boxes
57 | Modular GI box for 2 module | each | 22.5 | 0 | 22.5
58 | Modular GI box for 3 module | each | 30.5 | 0 | 30.5
59 | Modular GI box for 4 module | each | 37.5 | 0 | 37.5
60 | Modular GI box for 6 module | each | 50.5 | 0 | 50.5
61 | Modular GI box for 8 module | each | 65.5 | 0 | 65.5
62 | Modular GI box for 12 module | each | 80.5 | 0 | 80.5
PVC Boxes
63 | Modular box for 2 module | each | 18 | 0 | 18
64 | Modular box for 3 module | each | 24.5 | 0 | 24.5
65 | Modular box for 4 module | each | 30 | 0 | 30
66 | Modular box for 6 module | each | 40.5 | 0 | 40.5
67 | Modular box for 8 module | each | 52.5 | 0 | 52.5
68 | Modular box for 12 module | each | 64.5 | 0 | 64.5
Modular base & cover plate
69 | 1 Module | each | 53.5 | 30 | 37.45
70 | 2 Module | each | 53.5 | 30 | 37.45
71 | 3 Module | each | 68.5 | 30 | 47.95
72 | 4 Module | each | 54.5 | 30 | 38.15
73 | 6 Module | each | 77.5 | 30 | 54.25
74 | 8 Module ( 1 Row ) | each | 129.5 | 30 | 90.65
75 | 8 Module ( 2 Row ) | each | 130.5 | 30 | 91.35
76 | 9 Module | each | 151.5 | 30 | 106.05
77 | 12 Module | each | 184.5 | 30 | 129.15
Single Pole modular switch ISI marked
78 | 6 amps one way | each | 104 | 40 | 62.4
79 | 6 amps two way | each | 154 | 40 | 92.4
80 | 16 amps, one way | each | 174 | 40 | 104.4
Modular Sockets ISI marked
81 | 3 pin 5/6 amps | each | 130 | 40 | 78
82 | 6 pin 15/16 | each | 205 | 40 | 123
83 | 3 pin 25 amps | each | 253 | 40 | 151.8
PVC fastener
84 | 40 mm Long | each | 0.3 | 0 | 0.3
Steel fastener
85 | 6 mm X 75 mm | each | 5.5 | 0 | 5.5
86 | 8 mm X 75 mm | each | 7.3 | 0 | 7.3
Phenolic laminated sheet
87 | 3 mm thick | sqcm | 0.2 | 0 | 0.2
Ceilling Rose
88 | 2 Pate | each | 22 | 0 | 22
89 | 3 Pate | each | 28 | 0 | 28
Digital Time Switch
90 | 110 - 240 VAC 1 C/O Base/DIN 16 Pulse | each | 1895 | 20 | 1516
Contactor
91 | Two Pole 40A | each | 980 | 20 | 784
Metal Enclosures
92 | SP | each | 412 | 20 | 329.6
93 | DP | each | 600 | 20 | 480
94 | TP | each | 600 | 20 | 480
95 | FP | each | 600 | 20 | 480
Iron Screws
96 | 35 mm X 6 mm | each | 1.5 | 0 | 1.5
97 | 40 mm X 6 mm | each | 1.6 | 0 | 1.6
98 | 45 mm X 6 mm | each | 1.7 | 0 | 1.7
GI Saddles
99 | 19mm x 1 mm | each | 1.3 | 0 | 1.3
100 | 25mm x 1 mm | each | 1.6 | 0 | 1.6
Flat Iron
101 | 20 mm X 3 mm | kg | 33 | 0 | 33
102 | 25 mm X 3 mm | kg | 33 | 0 | 33
103 | 25 mm X 4 mm | kg | 33 | 0 | 33
104 | 25 mm X 6 mm | kg | 33 | 0 | 33
105 | 40 mm X 3 mm | kg | 33 | 0 | 33
106 | 50 mm X 6 mm | kg | 33 | 0 | 33
107 | 50 mm X 8 mm | kg | 33 | 0 | 33
G.I. Wire
108 | 6 SWG | kg | 56 | 0 | 56
109 | 8 SWG | kg | 55 | 0 | 55
110 | 10 SWG | kg | 56 | 0 | 56
111 | 12 SWG | kg | 57 | 0 | 57
Bolts & Nuts
112 | 25 mm X 3 mm | each | 2.2 | 0 | 2.2
113 | 32 mm X 8 mm | each | 4.3 | 0 | 4.3
114 | 38 mm X 7 mm | each | 5.15 | 0 | 5.15
115 | 38 mm X 10 mm | each | 7.25 | 0 | 7.25
Rag Bolts with Nuts
116 | 6 mm | each | 6 | 0 | 6
Brass Compression glands for 1.1 KV grade cable
117 | (28 mm) 3½ X 25 sq.mm | set | 59 | 0 | 59
118 | (32 mm) 3½ X 35 sq.mm | set | 70 | 0 | 70
119 | (35 mm) 3½ X 50 sq.mm | set | 89 | 0 | 89
120 | (38 mm) 3½ X 70 sq.mm | set | 108 | 0 | 108
121 | (45 mm) 3½ X 95 sq.mm | set | 135 | 0 | 135
122 | (25 mm) 4 X 10 sq. mm | set | 40 | 0 | 40
123 | (28 mm) 4 X 16 sq. mm | set | 59 | 0 | 59
124 | (28 mm) 4 X 25 sq. mm | set | 59 | 0 | 59
Aluminium Lugs for cable
125 | 6 sq. mm | each | 1 | 0 | 1
126 | 10 sq. mm | each | 1 | 0 | 1
127 | 16 sq. mm | each | 2 | 0 | 2
128 | 25 sq. mm | each | 2 | 0 | 2
129 | 35 sq. mm | each | 3 | 0 | 3
130 | 50 sq. mm | each | 4 | 0 | 4
131 | 70 sq. mm | each | 7 | 0 | 7
132 | 95 sq. mm | each | 8 | 0 | 8
Isolators ( DP)
133 | 25 A | each | 395 | 30 | 276.5
134 | 32 A | each | 430 | 30 | 301
135 | 40 A | each | 470 | 30 | 329
136 | 63 A | each | 625 | 30 | 437.5
137 | 100 A | each | 850 | 30 | 595
138 | 125 A | each | 965 | 30 | 675.5
Isolators ( FP)
139 | 32 A | each | 845 | 30 | 591.5
140 | 40 A | each | 1050 | 30 | 735
141 | 63 A | each | 1145 | 30 | 801.5
142 | 100 A | each | 1415 | 30 | 990.5
143 | 125 A | each | 1555 | 30 | 1088.5
DP RCBO 30 mA
144 | 10 A | each | 3980 | 30 | 2786
145 | 16 A | each | 3980 | 30 | 2786
146 | 20 A | each | 3980 | 30 | 2786
147 | 25 A | each | 3980 | 30 | 2786
148 | 32 A | each | 4170 | 30 | 2919
SPN DB With Metal door
149 | 4 Way | each | 1552 | 30 | 1086.4
150 | 8 Way | each | 1926 | 30 | 1348.2
151 | 12 Way | each | 2314 | 30 | 1619.8
VTPN DB With Metal door
152 | 4 Way | each | 9356 | 30 | 6549.2
153 | 6 Way | each | 10292 | 30 | 7204.4
154 | 8 Way | each | 11900 | 30 | 8330
155 | 12 Way | each | 16012 | 30 | 11208.4
Main Panel Board (Accoring to Drawing )
156 | Indoor wall mounted , type distribution boards made out of 2 mm thk. CR sheet metal painted with 2 coats of enamel paint | each | 9563 | 0 | 9563
MCCB 4P Icu 16 kA
157 | 63 A | each | 7166 | 30 | 5016.2
158 | 80 A | each | 7166 | 30 | 5016.2
159 | 100 A | each | 7166 | 30 | 5016.2
160 | 125 A | each | 7496 | 30 | 5247.2
161 | 160 A | each | 9260 | 30 | 6482
MCB 4P Icu 10 kA
162 | 32 A | each | 1732 | 30 | 1212.4
163 | 40 A | each | 2498 | 30 | 1748.6
164 | 63 A | each | 2498 | 30 | 1748.6
MCB TP Icu 10 kA
165 | 20 A | each | 1282 | 30 | 897.4
166 | 25 A | each | 1282 | 30 | 897.4
167 | 32 A | each | 1282 | 30 | 897.4
168 | 40 A | each | 1958 | 30 | 1370.6
169 | 50 A | each | 1958 | 30 | 1370.6
170 | 63 A | each | 1958 | 30 | 1370.6
MCB DP Icu 10 kA
171 | 10 A | each | 786 | 30 | 550.2
172 | 16 A | each | 786 | 30 | 550.2
173 | 20 A | each | 786 | 30 | 550.2
174 | 25 A | each | 786 | 30 | 550.2
175 | 32 A | each | 786 | 30 | 550.2
176 | 40 A | each | 1264 | 30 | 884.8
177 | 63 A | each | 1264 | 30 | 884.8
MCB SP Icu 10 kA
178 | 6 A | each | 262 | 30 | 183.4
179 | 10 A | each | 262 | 30 | 183.4
180 | 16 A | each | 262 | 30 | 183.4
181 | 20 A | each | 262 | 30 | 183.4
182 | 25 A | each | 262 | 30 | 183.4
183 | 32 A | each | 262 | 30 | 183.4
184 | 40 A | each | 574 | 30 | 401.8
Busbar ( Cupper )
185 | 100 A (16 X 5 ) mm | each | 394 | 0 | 394
186 | 125 A (18 X 6 ) mm | each | 492 | 0 | 492
187 | 150 A (20 X 7 ) mm | each | 590 | 0 | 590
Digital Measuring Instruiments
188 | Voltmeter | each | 506 | 20 | 404.8
189 | Ammeter | each | 546 | 20 | 436.8
Termination bar
190 | Termination bar | each | 73 | 20 | 58.4
Phase indicator L.E.D. lamps
191 | Phase indicator L.E.D. lamps | each | 41 | 20 | 32.8
Change over
192 | 63A, 4-POLE Change over | each | 2654 | 30 | 1857.8
Cut Out Fuse, 415-500V
193 | 63 A | each | 623 | 30 | 436.1
194 | 100 A | each | 756 | 30 | 529.2
195 | 160 A | each | 928 | 30 | 649.6
196 | 250 A | each | 1033 | 30 | 723.1
MS enclouser withj lock & key arrangements.
197 | For 63 A | each | 1180 | 20 | 944
198 | For 100 A | each | 1280 | 20 | 1024
199 | For 160 A | each | 1435 | 20 | 1148
200 | For 250 A | each | 1585 | 20 | 1268
Light Fittings
201 | 36W LED Recessed 2X2 | each | 4000 | 30 | 2800
LCTLRN-36-FO-CDL
202 | 18W squre LED Downlighter | each | 1550 | 30 | 1085
LSDN-18-CDL/TL/WW
203 | 6W Recess LED spot lights | each | 550 | 30 | 385
LSCRM-6W-CDL/NW/WW
204 | 12W Recess LED spot lights | each | 850 | 30 | 595
LSCRM-12W-CDL/NW/WW
205 | 12W Round/Squre Surface mounted LED | each | 1000 | 30 | 700
LCDSPLN-R-12-CDL
LCDSPLN-S-12-CDL
206 | 20W LED Batten lights fittings | each | 850 | 30 | 595
BN021C LED20S PSU CDL/NW GR
207 | 20 W LED Batten light | each | 865 | 30 | 605.5
LGT8-20-865-2
208 | Twin LED Batten Frame | each | 415 | 30 | 290.5
IGP132LT8-16
209 | 9W LED Bulb | each | 359 | 30 | 251.3
B22LED
Fan Fittings
210 | 1200 mm sweep celing fan | each | 2015 | 35 | 1309.75
9 Excel Star 1200mm White C/F
211 | 400 mm sweep High Flo Wall fan | each | 2500 | 35 | 1625
Esteem 400 mm Wall Fan
212 | 400 mm sweep cabin fan | each | 2584 | 35 | 1679.6
Gyro 400mm Cabin Fan
213 | 150 mm sweep heavy duty Exhust fan | each | 1850 | 35 | 1202.5
214 | 225 mm sweep heavy duty Exhust fan | each | 1965 | 35 | 1277.25
215 | 300 mm sweep heavy duty Exhust fan | each | 2150 | 35 | 1397.5
Hill Air 225mm
Holders
216 | Angle Holder | each | 30 | 30 | 21
217 | Batten Holder | each | 32 | 30 | 22.4
Fan Regulator
218 | Step type Fan Regulator | each | 198 | 40 | 118.8
Fan Hook
219 | fan-hook,by cutting roof slab and welding 10 mm dia. | each | 70 | 0 | 70
Call Bell
220 | Call bell Remote Controlled with Battery | each | 500 | 30 | 350
Dowm Rod
221 | Down Rod 600mm long | each | 150 | 0 | 150
Earthing Fittings
222 | 600 mm X 600 mm X 6.36 mm thick G.I. plate | each | 1438 | 0 | 1438
223 | 20 mm dia. G.I. pipe (medium class) | Mtr | 111 | 0 | 111
224 | CI/MS cover plate hinged to frame with Locking arrangement | each | 277 | 0 | 277
225 | Funnel | each | 19 | 0 | 19
226 | G.I. nuts and through bolts with washer | each | 26 | 0 | 26
227 | Charcoal | kg. | 8 | 0 | 8
228 | Salt | kg. | 8 | 0 | 8
229 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 4 | 0 | 4
230 | Cement | ton | 6300 | 0 | 6300
231 | Fine sand | cum | 806 | 0 | 806
232 | 600 mm X 600 mm X 3.18 mm thick copper plate (10.5 kg) | each | 5649 | 0 | 5649
233 | 25 mm X 5 mm G.I. strip (1.0 kg/mtr) | kg. | 57 | 0 | 57
234 | 40 mm dia. G.I. pipe (medium class) | Mtr | 239 | 0 | 239
235 | 40 mm dia. G.I. bend (medium class) | each | 57 | 0 | 57
236 | 15 mm dia. G.I. pipe (medium class) | Mtr | 88 | 0 | 88
237 | 8 SWG copper wire (4.0 mm dia) | kg. | 540 | 0 | 540
238 | GI saddle 20mm x 3mm | each | 2.5 | 0 | 2.5
239 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 0.5 | 0 | 0.5
240 | G.I. Hooks made of 8 SWG GI wire/ GI clip | each | 2 | 0 | 2
Others
241 | Cement, paint, sand etc. | LS/Mtr | 5 | 0 | 5

## labour (hidden)
LABOUR STATEMENT
S.l No | Description | Rate | Unit
1 | Unskilled
1.1 | Khallasi | 466 | /day
1.2 | Beldar/ coolie | 466 | /day
1.3 | Bhisti | 466 | /day
1.4 | Excavator | 466 | /day
1.5 | Mate | 466 | /day
2 | Semi Skilled
2.1 | Fitter, Grade 2 | 527 | /day
2.2 | Painter | 527 | /day
2.3 | Blacksmith, Grade 2 | 527 | /day
2.4 | Mason, Grade 2 | 527 | /day
2.5 | Stone Chiseler | 527 | /day
2.6 | Stone Breaker | 527 | /day
3 | Skilled
3.1 | Wireman | 617 | /day
3.2 | Cable jointer | 617 | /day
3.3 | Lineman | 617 | /day
3.4 | Fitter, Grade 1 | 617 | /day
3.5 | Carpenter, Grade 1 | 617 | /day
3.6 | Electrician | 617 | /day
3.7 | Electronic Technician | 617 | /day
3.8 | Welder | 617 | /day
3.9 | Store keeper | 617 | /day
4 | High Skilled
4.1 | Blaster (Special Class) | 679 | /day
4.2 | Mason (Special Class) | 679 | /day
4.3 | Blacksmith (Special Class) | 679 | /day
4.4 | Carpenter (Special Class) | 679 | /day
4.5 | Fitter (Special Class) | 679 | /day
4.6 | Painter (Special Class) | 679 | /day
4.7 | Welder (Special Class) | 679 | /day
4.8 | Plumber (Special Class) | 679 | /day
4.9 | Driller (Special Class) | 679 | /day
Referance :- ( for Area 'B' ) CONSTRUCTION OR MAINTENANCE OF ROADS OR RUNWAYS OR IN BUILDING OPERATIONS INCLUDING LAYING DOWN UNDERGROUND ELECTRIC, WIR.ELESS, RADIO, TELEVISION, TELEPHONE,TELEGRAPH AND OVERSEAS COMMUNICATION CABLES AND SIMILAR OTHER UNDERGROUND CABLING WORK, ELECTRIC LINES, WATER SUPPLY LINES AND SEWERAGE PIPE LINES.
File No. 1 /s8( 1) / 20 t3-LS-tI Government of India Ministry of Labour & Emplol,rnent OIfice of the Chief Labour Comrnissioner(C) New Delhi Dated::.28/09/2018 ORDER

## APPROVED LIST OF MATERIALS
APPROVED LIST OF MATERIALS
Sl.No. | ELECTRICALS
1 | 1100 Volts grade PVC insulated steel armoured and over all PVC sheathed cable. | Fort Gloster / NICCO / Havells / Asian Cables / Polycab / RETCO
2 | 1100 V grade PVC insulated stranded/ flexible multi standard copper wire with size in sq.mm. embossed on cable surface | Finolex / Havell’s/ RR KABLE
3 | Rigid PVC Conduit with ISI marked and accessories | PRECISION/ BEC/Harse
4 | Modular type 6 A & 16 A switch. 6 A & : 16 A socket, front plate, mounting box.Regulator/Dimmer | Wraparound of MK/ Mosaic of Legrand/ Ethena of Crabtree
5 | Switch fuse/fuse switch units | L&T /Hager/ LEGRAND .
6 | LT switch board | L&T / MDS / C&S/ Hager
7 | Protective Relays. | English Electric/GEC/Seimens/L&T
8 | Voltmeter and Ammeter | A.E / MDS
9 | Voltmeter and Ammeter Selector switch | Kaycee / MDS / L&T
10 | HRC Fuse. | Hager / L&T/ Legrand
11 | HRC fuse base and carries | Hager / L&T/ Legrand
12 | RCBO/MCCB/ MCB. | L&T / LEGRAND/ Hageer
13 | Isolator. | L&T / LEGRAND/ Hager
14 | Changeover Switch | L & T / LEGRAND/ Hager
15 | MCB Distribution Board | L&T/LEGRAND/Hager
16 | MCB/MCB type Isolator | L&T/ LEGRAND/Hager
17 | 30/32A DP moulded Isolat -ing Switch | Hager/ LEGRAND
18 | 15/5 Amp switch & plug socket | CRABERTEE / LEGRAND
19 | 15/5 Amp piano key type switch/flushed type plugsocket. | CRABERTEE / LEGRAND
20 | Ceiling Rose | Anchor / Cona
21 | Buzzer/Call Bell | Cona / L.K FUGA
22 | Electrical fitting fixtures | Philips /Crompton/ Wipro (Light),
Usha / Orient/ Crompton (fan)
23 | IC Cutout | Kec, Anker, gec