## ELECTRICAL
B.O.Q FOR ELECTRICAL WORK FOR UCO BANK , DISITAL BRANCH AT SALEPUR.
SL.NO. | DESCRIPTION OF ITEMS | UNIT | QUANTITY | RATE | AMOUNT
1.1 ELECTRICAL WIRING WORK
1 | Concealed / ressessed / surface light point / fan point / call bell point etc. wiring using 1100V FRLS grade 3R (P+N+E) x 1.5 Sq.mm FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling, with modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make. S.I.T.C.( Supply Installation Testing And Commissioning) as directed by the Engineer-in-charge. (Each circuit shall not feed more than 8 points OR 800 watts as per following configuration.)
NOTE:- 1. Only FRLS wire shall be used; 2. The wires from ceiling junction to light points / light fixture shall be drawn in flexible PVC conduit with adptor & cover for junction box & crimp type lugs at both the ends alongwith necessary hardware & accessories, etc. as required; 4. Looping of Neutral / Earth wire between two seperate Primary / Full Points is strictly not allowed; 5. Looping of Neutral / Earth wire between two seperate circuits on similar or other phase is strictly not allowed; 6. Ferulling / numbering / taggning to wires with circuit number & db name for all lighting & raw / ups power shall be strictly followed at both DB & switch board / switch socket boards ends.
1.1 | Primary light points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make. S.I.T.C. as directed by the Engineer-in-charge.( 1 light/fan controlled by one switch) | Nos. | 21
1.2 | Subsequent point ( Looped From Primary) | Nos | 10
1.3 | Independent point using one 6 Amp Modular Switch and one 6 Amp, 2/3 pin Modular scoket mounted on a sutable size Box for wall fans. | Nos | 4
1.4 | 6 Amp 2/3 pin Modular scoke with 6A Modular switch. ( on common switch Board.) | Nos. | 1
1.5 | Primary light points including the cost of clip in type 6A Modular switch of legrand mylinc or equivalent make & model as approved by project in charge. ( I light controlled by one switch UPS point ) | Nos. | 3
2 | Concealed raw power point using 6 Amp, 2/3 Pin Modular plug socket with 6 Amp Modular switch of legrand mylinc or equivalent make on separate board using galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI/PVC concealed back box, etc. Supply taken from Nearest L.D.B. Maximun 3 Points per Circuit for counter & Table | Nos | 4
3 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade multi standard FRLS copper wire run inside rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick of ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
3.1 | Concealed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( LDB to Common Switch board and Points) | Mts | 75
3.2 | Concealed wiring with ( 2Rx6.0 sqmm +1Rx4.0 sqmm copper wire ( PANEL to L.D.B.) | Mts | 15
1.2 COMPUTER WIRING WORK
1 | Supplt and fixing of concealed UPS power points using 1 nos. of 16 Amp, 3 Pin Modular switches to be provided on table top + 4 nos. 6 Amp Modular socket below table top of legrand mylinc or equivalent make taken from Nearest C.D.B with sutable size galvanized iron/PVC junction & switch boxes & clip in type modular type switch plate, GI/PVC concealed back box, etc. Maximun 3 Points per Circuit for counter & Table. S.I.T.C. as directed by the Engineer-in-charge. | SET | 4
2 | Concealed power point using 16 Amp 3 Pin plug socket with 16 Amp Modular switch of legrand mylinc or equivalent make mounted on separate board using suitable size galvanized iron junction & switch boxes & clip in type modular type switch plate,etc. Supply taken from R.D.B./ Nearest L.D.B. The point should not taken from any switch Board. S.I.T.C. as directed by the Engineer-in-charge. | Nos | 10
3 | Supplt and fixing of concealed UPS power points using clip in modular type 5 No. of 6/16 amp socket points controlled by 2 No of 16 amp modular switch with indicator of legrand mylinc or equivalent make taken from Nearest C.D.B with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed black box, etc. . The point should not from any switch Board S.I.T.C. as directed by the Engineer-in-charge. | SET | 1
4 | Supply of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated1100V FRLS grade 3R (P+N+E) x folling size FRLS multi stranded copper conductor PVC insulated wires (with proper R,Y,B color code) pulled through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick ISI mark laid concealed over false ceiling or in wall chases or on the ceiling in case of an open ceiling including of as required and multy stranded copper wire of folling size as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
4.1 | Concealed wiring with ( 2Rx2.5sqmm +1Rx1.5sqmm) copper wire ( C.D.B. to Computer Points ) | Mts | 180
4.2 | Concealed wiring with ( 2Rx4.0 sqmm +1Rx2.5sqmm) copper wire ( U.P.S. OUTPUT to C.D.B. ) | Mts | 30
1.3 A.C. WIRING WORK
1 | Supply & Installation of all required materials and wiring to Split AC 16 Amp 3 Pin Modulat socket mouted on suitable size concealed GI Box near to the AC controlled by 25 Amp DP isolator Enclosed in Powder coated DP Encloser of Legrand Ekinox3 model or Equivalent make taken from Nearest A.C..D.B/ M.L.D.B. with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed back box, etc. of legrand mylinc or equivalent make.The point should not taken from any switch Board S.I.T.C. as directed by the Engineer-in-charge. | Nos. | 2
2 | Supply of all required materials and wiring to 2 nos of Split AC point in System Room with 2 nos 16 Amp Modualar socket of legrand mylinc or equivalent make mouted on suitable size GI concealed Box controlled by 25 Amp Digital timer operated Alternatevly ( Alternate at every 4 hour) supplied by a 25 Amp RCBO Sensityvity 30mA Enclosed in 8 way SPN DB of Legrand or Equivalent make taken from Nearest M.L.D.B. with galvanized iron junction & switch boxes & clip in type modular type switch plate, switches, GI concealed back box, etc. .The point should not taken from any switch Board. S.I.T.C. as directed by the Engineer-in-charge. | Nos. | 1
2 | Supply and Installation of all required materials and wiring to circuits/ submains with following number and sizes of PVC insulated 1100 volt grade standard FRLS copper wire run through rigid FR/FRLS PVC conduits of 20mm Dia 1.5 mm thick ISI mark as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused and as per the direction of Consultant and Engineer-in-charge.
2.1 | Concealed wiring with 2 X 4sq. mm + 1 X 2.5sqmm copper wire ( From Msin Panel to 2.0 Ton Cassette /Split A.C. points through DP Isolator. ) | Mts | 70
2.PANEL BOARD & DISTRIBUTION BOARDS.
1 | Main Panel Board | Set | 1
Supply, delivery, installation , testing , commissioning , of L&T indoor wall ,floor , mounted , type distribution boards made out of 2 mm thk. CR sheet metal duely acid treated premised & painted with 2 coats of enamel paint compartment arrangement for each equipment & bus bar chamber on the top of the panel running horizontal through out its length duly lamp , vermin proof having provision cable by conduit entry , earthling stud as per specification mentioned below duly factory wired confirming to the relevant ISS & as per special condition of contract , making good the damages M.S. Cubical type Panel board should have hinged door at the front. The panel shall be provided with all accessories & following arrangements complete in all respect & direction of EIC (before fabrication of panel board drawing is to be approved by Engineer-in-charge).
Incoming-
1No 100A- 25KA - 4POLE -MCCB.
1 set of 100A TPN copper bus bar
1No 63A- 18KA - 4POLE -MCCB.
1 set of 63A TPN copper bus bar
63A, 4-POLE Change over
1 set of 63 A TPN copper bus bar
Out going-
1 Nos 40A, 4P MCB, for U.P.S.
1 Nos 40A, 4P MCB, Spare
4 Nos 25 A DP MCB for 2.0 ton Split A.C.
1 Nos 25 A DP MCB Spare
1 Nos 32 A DP MCB for L.D.B.
1 Nos 25 A DP MCB for Glow sign board & Outer Lighting
1 Nos 25 A DP MCB Spare
1 Nos 32 A DP MCB Spare
1No. VAF Digital meter with (100/5A)CT.
Cable tray.
Termination bar for each out put
6 Nos Phase indicator lamps
2 | Supply and installation of SPN, Double Door, Metal type, (hager IP43, legrand make Ekinox3 model or equivalent make as approved by SBIIMS), surface / flush mounted on wall, interconnected wiring complete with earthing lugs, including DB wiring, termination of circuits with ping type copper lugs, blank plates, etc. housing following switchgears :
2.1 | U.P.S Incoming DB | SET | 1
4 way SPN DB
40 Amp DP MCB – 2 nos (1main & 1 spare).
All MCB must be class C Type
2.2 | U.P.S Outgoing DB | SET | 1
6 way SPN DB
Incoming 1 No. 40A DP MCB
Out going 3 No. 25 A SP MCB
1 No. 10 A SP MCB
All MCB must be class C Type
2.3 | L.D.B (Light Distribution Board) | Set | 1
12 way SPN DB
Incoming :- 1 No. 32A DP MCB
Outgoing :- 10 No. 6-10 A SP MCB
All MCB must be class C Type
2.4 | C.D.B (Computer Distribution Board) | SET | 1
12 way SPN DB
Incoming :- 1 No. 32A DP-10 kA - MCB
Out going :- 10 No. 6-10 A SP -10 kA -MCB
All MCB must be class C Type
3. FITTINGS OF FIXTURES
1 | Supply,installation and testing of recess LED lights fittings ( 33 - 39 Wt) of squre type ( 2'-0"x2'-0") with all accessories complete of Philips/ Cropton /Wipro make as required as per direction of Engineer in charge. | Nos. | 10
2 | Supply,installation and testing of recess LED lights fittings ( 12Wt) of sport type with all accessories complete of Philips / Crompton/ Wipro as required as per direction of Engineer in charge. | Nos. | 14
3 | Providing and fitting of 450 mm sweep Wall fan of approved make . | Nos. | 4
4 | Providing and fitting of 400 mm sweep Exhust fan of approved make . | Nos. | 3
5 | Providing and fitting of call bell of approved make . | Nos. | 1
6 | Supply,installation and testing of LED light fittings (1x9wt) with angle holder of Philips/ Crompton/ Syska or equivelent as required as per direction of Engineer in charge. | Nos. | 4
7 | Supply & fixing of LED length of 5mt. Strip light with all accerrory. | Nos. | 11
4. EARTHING
1 | Providing and fixing Earthing with G.I. earth plate 600 mm X 600 mm X 6.36 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with alternative layer of 150mm thick charcoal/ coke and salt as required. For SPD/ Panel. | Nos. | 2
2 | Providing and fixing of Earthing with copper earth plate 600 mm X 600 mm X 3.18 mm thick including accessories, and providing masonry enclosurewith cover plate having locking arrangement and watering pipeof 2.7 metre long etc. with alternative layer of 150mm thick charcoal/ coke and salt as required. For UPS. | SET | 1
3 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including Connection / terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Mts | 15
4 | Providing and laying earth connection from earth electrode with 4.00 mm dia copper wire in 15 mm dia G.I. pipe from earth electrode including connection with copper thimble excavation and re-filling as required. | Mts. | 3
5 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing as required. | Mts. | 15
5.TELEPHONE WAIRING
1 | Supply , fixing , testing of phone point with suitable GI boxes with phone ,socket complete in all respect as per direction of EIC . | Nos. | 2
2 | Supply of all required materials & laying of the following sizes of phone wires of approved make inside the approved size PVC conduit complete in all respect as per instruction of EIC . 2 pairs telephone wires | Mtrs. | 30
6.DATA WAIRING
1 | Supply and laying of Cat6 4-pair 23AWG LSZH UTP Cable for data and voice in existing conduits/trunking. Make: Legrand/ Schneider/ Digisol | Mtr. | 280
2 | Supply , installation and testing of RJ-45Jack of Category 6 with Single-port British-style Modular Face Plate. Make: Legrand/ Schneider/ Digisol | Nos. | 15
3 | Supply , installation and testing of RJ-45Jack of Category 6 with Dual-port British-style Modular Face Plate. Make: Legrand/ Schneider/ Digisol | Nos. | 2
4 | Supply , installation and testing of Cat 6 24-port loaded Patch Panel.Make: Legrand/ Schneider/ Digisol | Nos. | 1
5 | Supply and Fixing of Cat6 Factory crimpped moulded 1mtr patch cord. Make: Legrand/ Schneider/ Digisol | Nos. | 17
6 | Supply and Fixing of Cat6 Factory crimpped moulded 2mtr patch cord. Make: Legrand/ Schneider/ Digisol | Nos. | 17
7 | Supply , installation and testing of 24port 10/100/1000Mbps L2 Unmanaged Switch with Four SFP Ports. Make: Cisco/ HP/ Digisol | Nos. | 1
8 | Supply & fixing 9 U wall mounted modem rack with power distribution box, cable manager, cantilever self, fan & mounting kit etc all complete. ( Make Valrack, Comrack, HCL ) | Set | 1
| TOTAL |  |  | Rs.
Total amount in words:-