# Vendor Name:-

Vendor Address:-

Product Company Name:-

Model No:-

Make:-

Date:-

Time:-

Mobile No:-

Name of Authorized Person:-

# DIGITAL FIRE & ELECTRONIC ALARM SYSTEM

GENERAL

The fire and electronic alarm system consists of control panel which is wired to various sensors like magnetic contact switch, vibration sensors, smoke sensors, heat sensors, panic switches and PIR sensors etc.  The type and number of sensors to be used depends on the size of area to be protected and the location of possible intrusion.

The control panel takes the decision of an alarm condition after getting the signal from the various sensors.  The control panel has capability to interface with the external devises like motorized sirens / hooters or the observation system lights etc.  The entire system operation is fully automatic under microprocessor technology.  The daily operations, user merely needs to just arm and disarm the system by turning a mechanical key/electronic switch.

The system shall be Electronic Regional Laboratory certified.

## The control panel

The fire and electronic alarm system control panel is the heart of the entire security system.  It shall monitor all system sensors and control alarm conditions.  The control panel shall have various visual indications on the front panels by LEDs.  If the alarm condition occurs the control panel should display which sensor caused alarm.  The panel should also display the mode of operation system i.e. arm / disarm.

Control panel should have 12 V - 7 Amp/ hrs automatically rechargeable sealed maintenance free batteries.  The control panel should have electronic switch / mechanical key for performing day to day operation i.e., day mode and night mode.

Control panel should be LCD based 12+1 fully programmable zone control panel with built in GSM, speech dialer with automatic arming and disarming and remote access through telephones. The control panel should be microcontroller based 16 zones programmable as delay, immediate, panic or fire along with one temper zone.  The system should have separate remote key pad with 16X4 LCD display.  There should be separate zone for fire detection.  The system should be programmable for the no. of seconds after which the panel response.  Automatic bypassing immediate and 24 hours active zone facility.  Panel can be armed and disarmed by telephone.  Code can be changed through telephone.  Any 8 electrical devises can be switched on or switched off through telephone.

## Features

- Arm and disarm mode

- Easy for operation just by mechanical key/electronic switch

- Battery backup for 36 hours

- Automatic switchover to battery in case of AC power failure

- Automatic battery charging once the AC power is restored

- Low battery indication

- Audio-visual alarm indication

- Different tones for fire and intruder alarm conditions

- Selectable delay time

- Close end circuits

- Speaker wire cut detection for all sensors and hooters/speakers/siren

- Supports combination of hooters/speakers/siren

- Open/short circuit detection on fire zones by audio-visual indication

- Provision for  interface with automatic telephone dialer/observation system etc. that to separately for fire and intruder alarm condition

- ERTL certified

## Input Devises

- Magnetic contact switch

Magnetic contact switch consists of two parts.  One consists of magnet and other contains the reed switch.  The magnet is mounted on the door (which moves) since no wire connections are required for connecting magnet.  The reed switch part is mounted on the door frame where the wire connections are made.  When the door is near the frame i.e., the door is closed the reed switch activates. When the door is opened the reed switch deactivates.  The deactivation breaks the reed switch contact which is detected by the control panel. Generally the range of the door sensor is ½ inch.

- Vibration Sensor

The vibration sensor detects vibration since the contact inside the sensor break due to vibration.  When the sensor is mounted on the walls/doors/windows any attempt to break, will be detected by the sensor.  Please note that if vibration detectors are to be connected they must be connected in 24 hours zone.

- Panic Switch

Panic switch should be either hand operated or foot operated.  In case of any threatening from the intruder / miscreants or to alert the people around the switch can be operated by pressure of hand/foot.

- Smoke Detector

The photo thermal smoke sensor range gives protection against both slow and fast developing fire and is an environmentally acceptable alternative to an ionization detector. It is a true multi criteria unit.  The output level from both the optical chamber and the thermisor are continually monitored by the on board processor, using algorithms developed specially for the unit.  An alarm signals is only enable in the detector once the processor is satisfied that an incipient fire has been detected. By using a combination of inputs the incidents of nuisance alarm is reduced while at the same time the response time to an actual fire is also improved. The system should have designed to be highly tolerant to the long term build up of the dust and other airborne contaminants.  The detector system shall have features like automatic drift compensation and alarm sensitivity adjustment.

- Heat Detector

A heat detector is a fire alarm device designed to respond when the convected thermal energy of a fire increases the temperature of a heat sensitive element. The thermal mass and conductivity of the element regulate the rate flow of heat into the element. All heat detectors have this thermal lag. Heat detectors have two main classifications of operation, "rate-of-rise" and "fixed temperature."

- PIR Sensor

PIR sensor should be dual element pyroelectric sensor with latest technology digital signal processor (DSP).  PIR should have pet immunity up to 25 Kg.  Detection range of PIR should be 15 mts with 110 degree angle.  The PIR sensor should have the sealed optics and selectable pulse count and excellent RFI and EMI immunity.  Activation of PIR sensor will be just through walk test.

Output Devise

- Hooter

Hooter is the external devise like multi tone electronic sounder can be connected to the control panel.  Minimum 8 different tones shall be programmable using DIP switches.  The hooter shall have a sound pressure level of 100 dB approximately, IP 54 environmental protection. The hooter activates in alarm condition.  Maximum of 2 speakers or their combination can be hooked to the system.  Individual hooter must be of 4 ohm impedance.

- Motorized siren

Motorized siren should be heavy duty and robust to withstand humidity and heat. It should be in suitable protective cage. It should be connected with the main control panel and direct electrical line.  The control panel will activate the connection of motorized siren with electricity.  The sound of motorized siren should travel 1 Km in ambit noise condition.

- Automatic telephone dial up

ATD require to dial pre-programmed telephone number on receipt of the trigger inputs by alarm system. It should work on GSM and also be capable of sending pre-coded / recorded SMS on mobile.  The features of ATD should be as follows:

- Tone and pulse dialing mode

- 10 programmable phone nos. up to 12 digit

- 2 separate messages for 2 different inputs like intruder and fire alarm

- Verification by playback recorded messages during programming

- Provision of parallel telephone instruments / GSM SIM

- Provision of programming from parallel telephone instruments as well as remote telephone instruments / mobile phone

- Ring detection before connecting to ATD

- Programmable password for entering mode

- Retention of programmed data in case of power failure

- Highest priority for condition dialing

## Technical Specification

| Sl. No. | Technical Specification Compliance for Fire and Electronic intruder Alarm System (Component and Description of Specification) | Compliance Yes/No |
| --- | --- | --- |
|  | CONTROL PANEL |  |
| 1 | LCD based minimum 12+1 fully programmable zone control panel with built in GSM speech dialer with automatic arming and disarming with remote access through telephone |  |
| 2 | Microcontroller based |  |
| 3 | Minimum 12+1 zones |  |
| 4 | Inbuilt GSM based speech and SMS dial up |  |
| 5 | Minimum 12 zones programmable as delay, immediate, panic or fire |  |
| 6 | One tamper zone |  |
| 7 | Separate remote key pad with 12X4 LCD display or more |  |
| 8 | Separate zone for fire detection and provision for connection of fire alarm system |  |
| 9 | Separate main control station for connection terminals and power supply units |  |
| 10 | Automatic arming and disarming facility |  |
| 11 | Can be operated through mobile and telephone line |  |
| 12 | Electrical devises can also be switched on or off through remote key pad |  |
| 13 | Built in battery backup |  |
| 14 | Zone omitting facility |  |
| 15 | Silent arming and night mode arming |  |
| 16 | Intrusion lock with time and date |  |
| 17 | Power failure indication |  |
| 18 | Blown fuse indication on LCD display on LED blinking on panel |  |
| 19 | Multiple sounder output |  |
| 20 | Distinct interrupted sounder output for fire alarm |  |
| 21 | Battery strength display with audio indication in case of low battery |  |
| 22 | GSM signal strength display |  |
| 23 | Walk test mode |  |
| 24 | Individual zone status is indicated in display |  |
| 25 | Independent entry delay time 2 to 240 sec |  |
| 26 | Independent exit delay time 2 to 240 sec |  |
| 27 | Sounder time 2 to 20 minutes and multiple sounder outputs |  |
| 28 | Speaker wire cut detection for all sensors and hooters and speakers |  |
| 29 | Support combination of hooters and speakers |  |
| 30 | Battery backup for 36 hours |  |
| 31 | Automatic switch off to battery in case of AC power failure |  |
| 32 | Automatic battery charging once the AC power is restored |  |
| 33 | ERTL certified. |  |
| Sl. No | SMOKE SENSOR & HEAT SENSOR |  |
| 1 | Automatic Drift compensation |  |
| 2 | Dust tolerant chamber provides optimum detection performance and minimal nuisance alarm between maintenance visit |  |
| 3 | Multifunction handheld remote programming and test tool |  |
| 4 | Sensitivity remotely programmable |  |
| 5 | Digital addressing capability |  |
| 6 | Remotely implemented advance maintenance features |  |
|  | Read and write last maintenance date |  |
|  | Read chamber contamination level |  |
|  | Read thermal element value alarm test |  |
| 7 | Selectable blink/no blink LED option via hand held tool |  |
| 8 | Photoelectric multi-criteria photo-thermal with 58 degree C and 78degree C fixed and rate of raise thermal detector |  |
| 9 | 8 to 30 VDC operating range enable operation in both fire and security system |  |
| 10 | -30 to +70 degree C operating temperature range |  |
| 11 | Multi-functional alarm – normal bio colour LED indicator |  |
| 12 | EN 54 certified |  |
| 13 | Make |  |

| Sl. No | AUTOMATIC TELEPHONE DIALER & BUILT IN VOICE & SMS GSM DIALER |  |
| --- | --- | --- |
| 1 | GSM speech & SMS dialer |  |
| 2 | Microcontroller base |  |
| 3 | 2 speech / voice messages |  |
| 4 | Separate intuition message |  |
| 5 | Minimum 10 programmable phone numbers upto 12 digits for intuition and fire message |  |
| 6 | 20 sec recording time for each message |  |
| 7 | Alarm SMS with alarm type, zone number with time and date information |  |
| 8 | System status SMS for arm and disarm |  |
| 9 | Power status SMS for AC power on and off, low battery |  |
| 10 | User editable name and address for alarm SMS |  |
| 11 | Message playback, telephone no editing facility, long volatile memory |  |
| 12 | Retention of programmed data in case of power failure |  |
| 13 | Highest priority for condition dialing and silent alarming |  |

| SL NO | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- |
|  | ELECTRICAL |  |
| 1 | Quiescent current: 30 mA Max. |  |
| 2 | Quiescent current with backlit LCD: 90 mA Max. |  |
| 3 | MAIN CONTROL STATION WITH ONE REMOTE KEY PAD |  |
| 4 | Quiescent current: 300 mA |  |
| 5 | Quiescent current with backlit LCD: 360 mA |  |
| 6 | Current with dialing: 530 mA Max. |  |
| 7 | Maximum sounder 1 current output : 1A |  |
| 8 | Maximum sounder 2 current output : 1A |  |
| 9 | Remote key pads : Up to three |  |
| 10 | Non-volatile Memory : Programming and Log |  |
| 11 | Zone response time : <500ms |  |
| 12 | Zone Loop Resistance : <5k ohm for NORMALLY CLOSED |  |
| 13 | Mains supply Voltage : 220+10%-15% 50Hz |  |
| 14 | Total current Output: 2A at 220V AC or 4A at 220V AC |  |
| 15 | Battery Voltage : 12V DC |  |
| 16 | Battery type : SMF Rechargeable |  |
| 17 | Battery Recharge Voltage: 13.8V +/-0.2V DC |  |
| 18 | ENVIRONMENTAL |  |
| 19 | Operating Temperature: 0C to 45C |  |
| 20 | Storage Temperature: -20C to 60C |  |
| 21 | Maximum humidity: 95% non-condensing |  |

| Sl No. | MAGNETIC CONTACT SENSOR |  |
| --- | --- | --- |
| 1 | Operating Gap: 15MM min |  |
| 2 | Contact Rating: 10W, 12/24VDC, 0.5A |  |
| 3 | Contact O/P : Normally Closed |  |
| 4 | 4 wire temper loop |  |

| Sl No. | PIR SENSOR |  |
| --- | --- | --- |
| 1 | Dual Element Pyroelectric sensor |  |
| 2 | Latest Technology Digital Signal Processor (DSP) |  |
| 3 | Pet Immunity up to 25 kg. |  |
| 4 | Detection Range 15m |  |
| 5 | Detection angle 110° |  |
| 6 | Sealed optics |  |
| 7 | Excellent RFI and EMI Immunity |  |
| 8 | Selectable Pulse Count |  |
| 9 | Walk Test |  |
| 10 | Detection range: 15m, 110° |  |
| 11 | RFI Immunity: Ave. 20V/m (10~1000MHz) |  |
| 12 | Power Supply: 9 ~ 16V DC, 12V Typical |  |
| 13 | Current Consumption: 20mA, 12V DC |  |
| 14 | Alarm Output: NC/NO 30V DC, 0.2A max. |  |
| 15 | Alarm Duration: 2 seconds |  |
| 16 | Pulse Count: Single/Double |  |
| 17 | Tamper Switch: Cover Open activation |  |
| 18 | Operating Temperature: 0° to 50° Celsius |  |
| 19 | Walk Test LED: Red, can disable |  |
| 20 | Temperature: Automatic using |  |
| 21 | Compensation: NTC thermistor |  |
| 22 | Detection Speed: 0.3 to 1 m/s |  |
| 23 | Reverse Polarity Protection: Through Diode |  |

| Sl No. | PANIC SWITCH |  |
| --- | --- | --- |
| 1 | Automatic reset (no key required) |  |
| 2 | Micro switch technology |  |
| 3 | In-built tamper switch |  |
| 4 | Contact O/P: NORMALLY CLOSED |  |
| 5 | Technology: micro-switch with roller |  |
| 6 | Tamper Switch: installed |  |

| Sl No. | HOOTER |  |
| --- | --- | --- |
| 1 | High power 130 db |  |
| 2 | 4 wired (with tamper loop) |  |
| 3 | Low current consumption |  |
| 4 | Available in 12V DC and 24V DC |  |
| 5 | Available in multiple tones |  |
| 6 | Weatherproof housing |  |

XXXXXXXXXXXXXXXXXXXXXXX